## Monthly_Fault_Data__Jan_Mar1
Date | Trip Time | Fault No | Location (Town) | Apparatus Tripped | Voltage Level(KV) | System Type | Substation Area | Weather | Time Reclosed | Downtime (Hours) | Reported By | Comments | Month | Severity | Fault type
2023-06-01 | 08:09 | 004/23 | Jwaneng | Jwaneng 132/33 T8: LV CB 8HO | 33 | Distribution | South | Clear | 08:51 | 0.7 | SCADA/Mosarwe | Bus zone trip | January | High | Permanent
2023-06-01 | 15:33 | 005/23 | Orapa | Orapa1 220/33 Transformer 2: LV CB H10 | 33 | Distribution | North | Rainy | 16:30 | 0.95 | SCADA/Theophilus | LV O/C trip, Winding Temp Trip & Oil Temp Alarm | January | High | Permanent
2023-07-01 | 11:35 | 007/23 | Sua Pan | Sua Pan 132/11 CBs 3L5 & 4L5 | 11 | Distribution | North | Clear | 19:56 | 8.35 | SCADA | Overcurrent protection, smoke on 11 busbar, Botash not importing | January | High | Permanent
17/01/2023 | 18:46 | 113/23 | Woodhall | Woodhall 132/11 Transformer 1A: LV CB 1HO | 11 | Distribution | Central | Cloudy | 23:29 | 4.717 | SCADA/Ramacha |  | January | High | Permanent
29/01/2023 | 22:38 | 016/23 | Orapa | Orapa 1 220/33 Transformer 2: LV CB H10 | 33 | Distribution | Central | Rainy | 23:25 | 0.85 | SCADA/MMUSI | 33 OVERVOLTAGE TRIP, Winding Temp Alarm & Trip Low set, Master trip | January | High | Permanent
2023-09-02 | 15:53 | 036/23 | Orapa | Orapa 2 GEN Tx 1: LV CB 01BAT10 | 11 | Distribution | North | Clear | 16:45 | 1.2 | SCADA/Batleng | DIFF protection operated | February | High | Permanent
17/02/2023 | 23:31 | 051/23 | Fancistown West | FWST 132/11 T1A & T2A: 11 CBs 1HOA & 2HOA | 11 | Distribution | North | Cloudy | 00:20 | 0.817 | SCADA/Serema | Earth Fault (E/F) protection trip | February | High | Permanent
18/02/2023 | 01:40 | 052/23 | Fancistown West | FWST 132/11 T1A & T2A: 11 CBs 1HOA & 2HOA | 11 | Distribution | North | Cloudy | 02:44 | 1.4 | SCADA/Serema | Earth Fault (E/F) protection trip recurrence | February | High | Permanent
14/03/2023 | 13:52 | 078/23 | Boteti | BDHT 132/11 Transformer 3 & Bus Section | 11 | Distribution | Central | Rainy | 14:36 | 0.73 | SCADA/Boteti | Buchholz trip, Oil surge, internal fault suspected | March | High | Permanent
15/03/2023 | 17:52 | 087/23 | Tlokweng | Tlokweng 132/11 Transformer 1: LV CB 1HO | 11 | Distribution | South | Clear | 18:40 | 0.8 | SCADA/Tlokweng | O/C trip, Master trip | March | High | Permanent
31/03/2023 | 06:02 | 096/23 | Woodhall | Woodhall 132/33 TRF 3: HV CB 310 & LV CB H30 | 33 | Distribution | South | Cloudy | ARC | 0 | SCADA | No time reclosed likely no restoration indication; breaker sequence: Tripped | March | Low | Transient
18/04/2022 | 3:26 | 117/23 | Kanye | Kanye 132/11 kV Transformer 1: LV CB 1HO | 11 | Distribution | South | Clear | 5:42 | 1.27 | SCADA/Baoki | Trip was due to a through fault from feeder 4L5. | April | High | Permanent
18/04/2022 | 3:26 | 117/23 | Kanye | Kanye 132/11 kV Transformer 2: LV CB 2H0 | 11 | Distribution | South | Clear | 5:42 | 1.27 | SCADA/Baoki | Trip was due to a through fault from feeder 4L5. | April | High | Permanent
18/04/2022 | 7:35 | 118/23 | Kanye | Kanye 132/11 kV Transformer 1: LV CB 1HO | 11 | Distribution | South | Clear | 8:19 | 0.73 | SCADA/Baoki | Trip was due to a through fault from feeder 4L5. Further patrolling carried out. | April | High | Permanent
18/04/2022 | 7:35 | 118/23 | Kanye | Kanye 132/11 kV Transformer 2: LV CB 2H0 | 11 | Distribution | South | Clear | 8:19 | 0.73 | SCADA/Baoki | Trip was due to a through fault from feeder 4L5. Further patrolling carried out. | April | High | Permanent
2023-07-04 | 8:07 | 105/23 | BDHT | BDHT 132/11kV Transformer 1 | 11 | Distribution | South | Clear | 9:02 | 0.95 | SCADA / Ntoko |  | April | High | Permanent
2023-07-04 | 8:07 | 105/23 | BDHT | BDHT 132/11kV Transformer 4 | 11 | Distribution | South | Clear | 9:00 | 0.92 | SCADA |  | April | High | Permanent
2023-07-04 | 8:07 | 105/23 | MOGS | MOGS 132/33kV Transformer 1 | 33 | Distribution | South | Clear | 9:01 | 0.93 | SCADA |  | April | High | Permanent
2023-07-04 | 8:07 | 105/23 | MOGS | MOGS 132/33kV Transformer 2 | 33 | Distribution | South | Clear | 9:01 | 0.93 | SCADA |  | April | High | Permanent
2023-11-04 | 3:17 | 111/23 | MORP | Morp A Generator 2 12kv CB 2GO | 12 | Distribution | Central | Clear | 10:51 | 7.57 | SCADA / Ralesota | Load loss: 20 MW, 151.3 MWh | April | High | Permanent
26/04/2023 | 17:19 | 121/23 | Jwaneng | Jwaneng 132/33kV Transformer 9 HV CB 410 | 33 | Distribution | South | Clear | 18:02 | 0.72 | SCADA / Mosarwe | Load loss to Debswana Mine Boreholes power supply. | April | High | Permanent
26/04/2023 | 17:19 | 121/23 | Jwaneng | Jwaneng 132/33kV Transformer 9 LV CB 9H0 | 33 | Distribution | South | Clear | 18:02 | 0.72 | SCADA / Mosarwe | Load loss to Debswana Mine Boreholes power supply. | April | High | Permanent
2023-05-05 | 15:15 | 124/23 | B/HURST | B/HURST 132/11kV Transformer 2 LV CB 4H0 | 11 | Distribution | South | Clear | 17:05 | 1.83 | SCADA/MAKOKO | Intertrip Receive/Send; Tripped | May | High | Permanent
2023-05-05 | 15:15 | 124/23 | MOGS | MOGS 132/11kV Transformer 3 HV CB 410 | 11 | Distribution | South | Clear | 17:08 | 1.88 | SCADA | Intertrip Receive; Tripped | May | High | Permanent
2023-05-05 | 15:15 | 124/23 | MOGS | MOGS 132/11kV Transformer 3 LV CB 3H0 | 11 | Distribution | South | Clear | 17:13 | 1.97 | SCADA | Tripped | May | High | Permanent
2023-05-05 | 15:15 | 124/23 | MOGS | MOGS 132/11kV Transformer 4 HV CB 510 | 11 | Distribution | South | Clear | 17:08 | 1.88 | SCADA | Intertrip Receive; Tripped | May | High | Permanent
2023-05-05 | 15:15 | 124/23 | MOGS | MOGS 132/11kV Transformer 4 LV CB 4H0 | 11 | Distribution | South | Clear | 17:13 | 1.97 | SCADA | Tripped | May | High | Permanent
2023-08-05 | 0:16 | 128/23 | Mowana | Mowana 132/11kV Transformer 1 | 11 | Distribution | IPS | Clear | 5:22 | 5.1 | SCADA | Overvoltage; Tripped | May | High | Permanent
2023-08-05 | 0:13 | 128/23 | Orapa | Orapa 2 220/33kV Transformer 1 HV CB H10 | 33 | Distribution | IPS | Clear | 5:41 | 5.47 | SCADA | Overvoltage; Tripped | May | High | Permanent
31/05/2023 | 5:14 | 140/23 | Gov/Enclave | Gov/Enclave 132/11kV TRF 2 HV CB 280 | 11 | Distribution | South | Cloudy | 15:03 | 9.82 | SCADA/Ntoko | Master Trip Operated; Tap Change Buchholz Operated | May | High | Permanent
31/05/2023 | 5:14 | 140/23 | Gov/Enclave | Gov/Enclave 132/11kV TRF 2 LV CB 2HO | 11 | Distribution | South | Cloudy | 15:03 | 9.82 | SCADA/Ntoko | Under Frequency; Protection Trip | May | High | Permanent
2023-02-06 | 10:48 | 141/23 | Maun | Maun 132/11kV Transformer 1 HV CB 110 | 11 | Distribution | North | Clear | 11:25 | 0.62 | SCADA/MOSALA | Did not trip initially; High set O/C on Matshwane feeder; later tripped | June | High | Permanent
2023-02-06 | 10:48 | 141/23 | Maun | Maun 132/11kV Transformer 2 LV CB 2TO | 11 | Distribution | North | Clear | 11:25 | 0.62 | SCADA/MOSALA | O/C trip | June | High | Permanent
15/06/2023 | 15:18 | 147/23 | Makoba | Makoba 132/33kV T2 HV & LV CBs 210 & T20 | 33 | Distribution | North West | Clear | 15:40 | 0.37 | SCADA/Chabalala | LV Bus zone 2 trip & Mastertrip operated | June | Medium | Sustained
15/06/2023 | 15:18 | 147/23 | Makoba | 33kV Bus Bar B/S CB S10 | 33 | Distribution | North West | Clear | 15:40 | 0.37 | SCADA/Chabalala | Zone 2 trip, Check Zine trip & Zone 2 trip L1 | June | Medium | Sustained
29/06/2023 | 2:28 | 154/23 | Motheo Mine | Motheo Mine 11kV B/Section CB 1SO | 11 | Distribution | North West | Clear | 4:07 | 1.65 | Scada/CSS | No indication; Tripped | June | High | Permanent
08/08/2023 | 03:35 | 150/23 | Morupule A | Morupule A Generator 3 11kV CB 3G0 | 11 | Distribution | Central | Clear | TBA | 0 | SCADA | Thermal Stress; Tripped | August | Low | Transient
23/09/2023 | 21:26 | 162/23 | Kgale View | Kgale View T1 & T2 11kV LV CB 1H0 | 11 | Distribution | South | Clear | 00:24 | 2.97 | Scada / Galetshetse | Arc protection; TRIP | September | High | Permanent
23/09/2023 | 21:26 | 162/23 | Kgale View | Kgale View T1 & T2 11kV LV CB 2H0 | 11 | Distribution | South | Clear | 23:03 | 1.62 | SCADA/Galetshetse | Arc protection; TRIP | September | High | Permanent
23/09/2023 | 21:26 | 162/23 | Kgale View | Kgale View B/section CB 1SO | 11 | Distribution | South | Clear | 00:24 | 2.97 | SCADA/Galetshetse | Arc protection; TRIP | September | High | Permanent
24/09/2023 | 06:08 | 163/23 | Karowe | Karowe T1 LV CB 1T0 | 11 | Distribution | North | Clear |  | 0 | SCADA/Phillip | TRIP (No load loss as B/Section CB 1SO was closed) | September | Low | Transient
28/09/2023 | 18:55 | 164/23 | Phakalane | Phakalane T1B LV CB 1HOB | 11 | Distribution | South | Clear | 19:00 | 0.08 | SCADA/Selei | Buchholz Alarm; TRIP | September | Low | Transient
05/10/2023 | 12:37 | 168/23 | BDHT | BDHT 132/11kV Transformer 1 | 11 | Distribution | South | Clear | 13:15 | 0.63 | SCADA / Ntoko | Zone 1,2,3 Trip, Master Trip, Underfreq | October | High | Permanent
17/11/2023 |  | 191/23 | Gab East | Gab East 132/11kV T2B LV CB 2HOB | 11 | Distribution | South | Clear | 07:58 | 1.95 | SCADA / Ntoko | Trip | November | High | Permanent
17/11/2023 |  | 191/23 | Gab East | 11kV Bussection CB 1SOB | 11 | Distribution | South | Clear | 08:15 | 2.18 | SCADA / Ntoko | Master trip, Buszone trip, Trip Circuit Supervision 1 | November | High | Permanent
18/11/2023 |  | 192/23 | Gab East | Gab East 132/11kV T1B LV CB 1HOB | 11 | Distribution | South | Clear | 02:57 | 2.27 | SCADA / Ntoko | Buszone operated, VT Fail | November | High | Permanent
18/11/2023 |  | 192/23 | Gab East | Gab East 132/11kV T2B LV CB 2HOB | 11 | Distribution | South | Clear | 02:58 | 2.28 | SCADA / Ntoko | Tripped | November | High | Permanent
18/11/2023 |  | 192/23 | Gab East | Gab East 132/11kV T3B LV CB 3HOB | 11 | Distribution | South | Clear | 02:58 | 2.28 | SCADA / Ntoko | Tripped | November | High | Permanent
18/11/2023 |  | 192/23 | Gab East | Gab East 11kV CB 1SOB | 11 | Distribution | South | Clear | 02:58 | 2.28 |  | Phase A & B trip, Buszone Phase B and C | November | High | Permanent
12/12/2023 | 17:51 | 206/23 | Morupule A | Morp.A Unit 2 12kV CB 2GO | 12 | Distribution | Central | Clear | TBA | 0 | SCADA | Flame failure; TRIPPED | December | Low | Transient
15/12/2023 | 17:06 | 206/23 | Hydromet | Hydromet 66/33kV TRF 01 HV CB H10 | 33 | Distribution | North | Clear | 18:54 | 1.8 | Scada/Kahona/Chabalala | Tertiary E/Fault, Master Trip; TRIPPED | December | High | Permanent
15/12/2023 |  | 206/23 | Hydromet | Hydromet 66/33kV TRF 01 LV CB 180 | 33 | Distribution | North | Clear | 18:54 | 1.8 | Scada/Kahona/Chabalala | Tertiary E/Fault, Master Trip; TRIPPED | December | High | Permanent
15/12/2023 |  | 206/23 | Hydromet | 33kV Bus Coupler CB 130 | 33 | Distribution | North | Clear | 18:04 | 0.97 | SCADA/Kahona | Closed to restore supply via TX 03 | December | High | Permanent
23/12/2023 | 14:38 | 211/23 | Morupule A | Morp.A Unit 1 12kV CB 1GO | 12 | Distribution | Central | Clear | TBA | 0 | SCADA | Furnace pressure high; TRIPPED | December | Low | Transient
25/12/2023 | 09:50 | 211/23 | Orapa 1 | Orapa 1 220/33 kV Tx 3: HV CB H30 | 33 | Distribution | Central | Rainy | 13:58 | 4.13 | SCADA/Likokoto | Tap changer overpressure trip; Water ingress found on overpressure termination box | December | High | Permanent
27/12/2023 | 00:39 | 213/23 | Morupule A | Morupule A 12kV CB 3GO | 12 | Distribution | Central | Cloudy | 05:05 | 4.43 | Obed | Generator temperature high; Tripped | December | High | Permanent
04/01/2024 | 02:10 | 005/24 | Gaphatshwa | 132/11kV T3 CB 3H0 | 11 | Distribution | South | Clear | 03:51 | 1.68 | SCADA/Ntoko | TRIP | January | High | Permanent
04/01/2024 | 05:23 | 005/24 | Gaphatshwa | 132/11kV T4 CB 4H0 | 11 | Distribution | South | Clear | 03:51 | 1.68 | SCADA/Ntoko | TRIP | January | High | Permanent
07/01/2024 | 11:52 | 008/24 | F/Town West | F/Town West 132/11kV Transformer 1 : LV CB 1HOA | 11 | Distribution | North | Clear | 12:53 | 1.02 | SCADA/Chabalala | master trip, High set O/C, On Bus Section CB - High set O/C; Tripped | January | High | Permanent
07/01/2024 | 11:52 | 008/24 | F/Town West | 11kV B/Section : CB 1S0A | 11 | Distribution | North | Clear | 12:53 | 1.02 | SCADA/Chabalala | Tripped | January | High | Permanent
15/01/2024 | 22:15 | 019/24 | Ghanzi | Ghanzi 132/11kV T1 LV CB 1H0 | 11 | Distribution | South | Cloudy | 3:43 | 5.47 | Rasefako | Phase B-C O/C protetction; Tripped | January | High | Permanent
15/01/2024 | 22:15 | 019/24 | Ghanzi | Ghanzi 132/11kV T2 LV CB 2H0 | 11 | Distribution | South | Cloudy | 3:43 | 5.47 | Rasefako | Phase B-C O/C protetction; Tripped | January | High | Permanent
16/01/2024 | 10:00 | 023/24 | Ramotswa | Ramotswa 132/11kV T3 HV CB 310 | 11 | Distribution | South | Clear | 10:27 | 0.45 | SCADA/Ntoko | Zone 1,2,3 Trip, Master Trip, Underfreq; Tripped | January | Medium | Sustained
16/01/2024 | 10:00 | 023/24 | Ramotswa | Ramotswa 132/11kV T3 LV CB 3H0 | 11 | Distribution | South | Clear | 10:27 | 0.45 | SCADA/Ntoko | Zone 1,2,3 Trip, Master Trip, Underfreq; Tripped | January | Medium | Sustained
26/01/2024 | 08:34 | 028/24 | Jwaneng | Jwaneng 132/33 kV Transformer 8: LV CB 8H0 | 33 | Distribution | South | Clear | 09:04 | 0.5 | SCADA / Baikgantshi | 33kV bus zone: R-ɸ start, 89 alarm, 87 DIFF start, breaker fail, W-ɸ start, B-ɸ trip, zone 1 trip; Tripped | January | Medium | Sustained
26/01/2024 | 08:34 | 028/24 | Jwaneng | 33kV Cap Bank 2 CB 4L5 | 33 | Distribution | South | Clear | 09:17 | 0.72 | SCADA / Baikgantshi | Tripped | January | High | Permanent
26/01/2024 |  | 028/24 | Jwaneng | Jwaneng 132/33 kV Transformer 8: HV CB 110 | 33 | Distribution | South | Clear |  | 0 | SCADA / Baikgantshi | Did not trip | January | Low | Transient
26/01/2024 | 12:38 | 029/24 | Gab East | Gab EAST 132/11 kV Transformer 2B: HV CB 210B | 11 | Distribution | South | Clear | 13:15 | 0.62 | SCADA / Makoko | Did not trip initially; Tripped | January | High | Permanent
26/01/2024 | 12:38 | 029/24 | Gab East | LV CB 2H0B | 11 | Distribution | South | Clear | 13:16 | 0.63 | SCADA / Makoko | Instateneous trip; Tripped | January | High | Permanent
26/01/2024 | 12:38 | 029/24 | Gab East | 11 kV Bus Section CB 1S0B | 11 | Distribution | South | Clear | 13:18 | 0.67 | SCADA / Makoko | L/H bus zone 3ɸ trip, Centre zone trip, bus zone A & B trip; Tripped | January | High | Permanent
2024-02-07 | 17:59 | 041/24 | Ghanzi | Ghanzi Tx 1 LV CB 1H0 | 11 | Distribution | NW | Clear | 18:44 | 0.75 | SCADA | O/C trip; Through fault from feeder 2L5 | February | High | Permanent
2024-02-07 | 17:59 | 041/24 | Ghanzi | Ghanzi Tx 2 LV CB 2H0 | 11 | Distribution | NW | Clear | 18:44 | 0.75 | SCADA | O/C trip | February | High | Permanent
2024-02-11 | 10:03 | 046/24 | GAB EAST | Tx 2B HV CB 210B | 11 | Distribution | South | Clear | 10:42 | 0.65 | SCADA/Makoko | Tripped | February | High | Permanent
2024-02-11 | 11:00 | 046/24 | GAB EAST | Tx 2B LV CB 2H0B | 11 | Distribution | South | Clear | 11:29 | 0.48 | SCADA/Makoko | Tripped again during restoration | February | Medium | Sustained
2024-02-11 | 11:00 | 046/24 | GAB EAST | 11kV Bus Section CB 2S0B | 11 | Distribution | South | Clear | 11:29 | 0.48 | SCADA/Makoko | Phase A–C trip, bus zone trip | February | Medium | Sustained
2024-02-17 | 21:02 | 049/24 | Gaphatshwa | Gaphatshwa T4 11kV CB 4HO | 11 | Distribution | South | Clear | 22:21 | 1.32 | E. NTOKO/SCADA | Overvoltage trip; Feeder 10L5 conductor down | February | High | Permanent
2024-02-26 | 07:07 | 037/24 | Mmakgodumo | Mmakgodumo T1 LV CB H10 | 33 | Distribution | South | Clear | 09:52 | 2.75 | SCADA/Baoki | OC & E/F Phase B&C; Load loss (4 MW) | February | High | Permanent
2024-02-26 | 07:07 | 037/24 | Mmakgodumo | Mmakgodumo T2 LV CB H20 | 33 | Distribution | South | Clear | 11:37 | 4.5 | SCADA/Baoki | OC & E/F Phase B&C; Load loss (4 MW) | February | High | Permanent
2024-03-16 | 21:08 | 058.3/24 | Tlokweng | Tlokweng T1 HV & LV CBs 110 & 1H0 | 11 | Distribution | South | Clear | 00:37 | 3.48 | SCADA/Mangole | Under voltage trip | March | High | Permanent
2024-03-16 | 21:08 | 058.3/24 | Tlokweng | Tlokweng T2 HV & LV CBs 210 & 2H0 | 11 | Distribution | South | Clear | 00:37 | 3.48 | SCADA/Mangole | Under voltage trip | March | High | Permanent
2024-03-16 | 21:08 | 058.3/24 | Gaphatshwa | Gaphatshwa T3 & T4 HV CBs 410 & 210; LV CBs 3H0 & 4H0 | 11 | Distribution | South | Clear | 01:35 | 4.45 | SCADA/Makoko | Low set E/F trip | March | High | Permanent
2024-03-30 | 17:05 | 062/24 | Kanye | Kanye T1 LV CB 1HO | 11 | Distribution | South | Clear | 21:22 | 4.28 | SCADA/Mosarwe/Baoki | OC & E/F trip; Load loss (5.8 MW) | March | High | Permanent
2024-03-30 | 17:05 | 062/24 | Kanye | Kanye T1 HV CB 180 | 11 | Distribution | South | Clear | NIL | 0 | SCADA/Mosarwe/Baoki | DID NOT TRIP | March | Low | Transient
2024-03-30 | 17:05 | 062/24 | Kanye | Kanye T2 LV CB 2HO | 11 | Distribution | South | Clear | 17:50 | 0.75 | SCADA/Mosarwe/Baoki | OC & E/F trip | March | High | Permanent
2024-03-30 | 17:05 | 062/24 | Kanye | Kanye T2 HV CB 280 | 11 | Distribution | South | Clear | NIL | 0 | SCADA/Mosarwe/Baoki | DID NOT TRIP | March | Low | Transient
2024-03-16 | 21:08 | 058.3/24 | Tlokweng | Tlokweng T1 HV & LV CBs 110 & 1H0 | 11 | Distribution | South | Clear | 00:37 | 3.48 | SCADA/Mangole | Under voltage trip | March | High | Permanent
2024-03-16 | 21:08 | 058.3/24 | Tlokweng | Tlokweng T2 HV & LV CBs 210 & 2H0 | 11 | Distribution | South | Clear | 00:37 | 3.48 | SCADA/Mangole | Under voltage trip | March | High | Permanent
2024-03-16 | 21:08 | 058.3/24 | Gaphatshwa | Gaphatshwa T3 & T4 HV CBs 410 & 210; LV CBs 3H0 & 4H0 | 11 | Distribution | South | Clear | 01:35 | 4.45 | SCADA/Makoko | Low set E/F trip | March | High | Permanent
2024-03-30 | 17:05 | 062/24 | Kanye | Kanye T1 LV CB 1HO | 11 | Distribution | South | Clear | 21:22 | 4.28 | SCADA/Mosarwe/Baoki | OC & E/F trip; Load loss (5.8 MW) | March | High | Permanent
2024-03-30 | 17:05 | 062/24 | Kanye | Kanye T1 HV CB 180 | 11 | Distribution | South | Clear | NIL | 0 | SCADA/Mosarwe/Baoki | DID NOT TRIP | March | Low | Transient
2024-03-30 | 17:05 | 062/24 | Kanye | Kanye T2 LV CB 2HO | 11 | Distribution | South | Clear | 17:50 | 0.75 | SCADA/Mosarwe/Baoki | OC & E/F trip | March | High | Permanent
2024-03-30 | 17:05 | 062/24 | Kanye | Kanye T2 HV CB 280 | 11 | Distribution | South | Clear | NIL | 0 | SCADA/Mosarwe/Baoki | DID NOT TRIP | March | Low | Transient
2024-05-04 | 04:23 | 071/24 | Mogoditshane | Mogoditshane T3 HV CB 410 | 11 | Distribution | South | Clear | 2:42 | 1.68 | SCADA/Galetshetse | Tripped; Load loss (6 MW) | May | High | Permanent
2024-05-04 | 04:23 | 071/24 | Mogoditshane | Mogoditshane T3 LV CB 3H0 | 11 | Distribution | South | Clear | 2:42 | 1.68 | SCADA/Galetshetse | Tripped | May | High | Permanent
2024-05-04 | 04:23 | 071/24 | Mogoditshane | Mogoditshane T4 HV CB 510 | 11 | Distribution | South | Clear | 2:42 | 1.68 | SCADA/Galetshetse | Tripped | May | High | Permanent
2024-05-04 | 04:23 | 071/24 | Mogoditshane | Mogoditshane T4 LV CB 4H0 | 11 | Distribution | South | Clear | 2:42 | 1.68 | SCADA/Galetshetse | Tripped | May | High | Permanent
2024-05-24 | 20:36 | 077/24 | Francistown West | F/Town West T1A LV CB 1HOA | 11 | Distribution | North | Clear | 22:31 | 1.92 | SCADA/Makoko | Tripped; Load loss (8.7 MW) | May | High | Permanent
2024-05-24 | 20:36 | 077/24 | Francistown West | F/Town West T2A LV CB 2HOA | 11 | Distribution | North | Clear | 22:33 | 1.95 | SCADA/Makoko | Tripped | May | High | Permanent
2024-05-31 | 07:51 | 079/24 | Gab East | Gab East T1A HV CB 110A | 11 | Distribution | South | Clear | 08:37 | 0.77 | SCADA/R. Galetshetse | LV REF trip; Load loss (10 MW) | May | High | Permanent
2024-05-31 | 15:35 | 079/24 | Orapa | Orapa 2 T1 HV CB H10 | 33 | Distribution | North | Clear | 18:46 | 3.18 | SCADA/Maduo | Master trip; Load loss (15 MW) | May | High | Permanent
2024-05-31 | 15:35 | 079/24 | Orapa | Orapa 2 T1 LV CB H08 | 33 | Distribution | North | Clear | 18:50 | 3.25 | SCADA/Louis | E/F trip | May | High | Permanent
2024-06-01 | 16:50 | 080/24 | Woodhall | Woodhall T3 LV CB H30 | 33 | Distribution | North | Clear | ARC | 0 | SCADA/Ramacha | LV CB Close block | June | Low | Transient
2024-06-04 | 05:07 | 082/24 | Lobatse | Lobatse T2A HV CB 210 | 11 | Distribution | South | Clear | 03:41 | 1.43 | SCADA/Ramacha | Tripped; Load loss | June | High | Permanent
2024-06-04 | 05:07 | 082/24 | Lobatse | Lobatse T2A LV CB 2H0 | 11 | Distribution | South | Clear | 03:41 | 1.43 | SCADA/Ramacha | Tripped | June | High | Permanent
2024-06-07 | 07:51 | 082/24 | Gab East | Gab East T1A HV CB 110A | 11 | Distribution | South | Clear | 08:37 | 0.77 | SCADA/R. Galetshetse | LV REF trip; Load loss (10 MW) | June | High | Permanent
2024-06-07 | 07:51 | 082/24 | Gab East | Gab East T1A LV CB 1H0A | 11 | Distribution | South | Clear | 08:37 | 0.77 | SCADA/R. Galetshetse | LV REF trip | June | High | Permanent
2024-06-17 | 09:41 | 083/24 | Maun | Maun T1 LV CB 1T0 | 11 | Distribution | North | Clear | 11:08 | 1.45 | SCADA/Sekgatlhola | Tripped | June | High | Permanent
2024-06-17 | 09:45 | 083/24 | Maun | Maun T2 HV CB 210 | 11 | Distribution | North | Clear | 10:59 | 1.23 | SCADA/Sekgatlhola | Master trip; Main protection operated | June | High | Permanent
2024-06-17 | 09:45 | 083/24 | Maun | Maun T2 LV CB 2T0 | 11 | Distribution | North | Clear | 11:05 | 1.33 | SCADA/Sekgatlhola | Tripped | June | High | Permanent
2024-06-28 | 15:03 | 084/24 | Ghanzi | Ghanzi T1 HV CB 110 | 11 | Distribution | North | Clear | 15:25 | 1.45 | SCADA/Rasefako | Main Trip Circuit Fail; Load loss (17.9 MW) | June | High | Permanent
2024-06-28 | 15:03 | 084/24 | Ghanzi | Ghanzi T1 LV CB 1H0 | 11 | Distribution | North | Clear | 15:25 | 1.45 | SCADA/Rasefako | HV trip received | June | High | Permanent
2024-06-28 | 15:03 | 084/24 | Ghanzi | Ghanzi Bus Section CB 1S0 | 11 | Distribution | North | Clear | 15:25 | 1.45 | SCADA/Rasefako | Buszone protection ABC | June | High | Permanent
2024-07-04 | 17:59 | 085/24 | FWST | FWST T2A LV CB 2H0A | 11 | Distribution | North | Clear | 18:33 | 0.58 | SCADA/Chawilani | Overload due to T1A outage; 75% load restored | July | High | Permanent
2024-07-05 | 06:26 | 086/24 | Tlokweng | Tlokweng T1 HV CB 110 | 11 | Distribution | South | Cloudy | 09:35 | 3.15 | SCADA/Galetshetse | Master trip; winding & REF trip | July | High | Permanent
2024-07-05 | 06:26 | 086/24 | Tlokweng | Tlokweng T1 LV CB 1HO | 11 | Distribution | South | Cloudy | 03:17 | 3.15 | SCADA/Galetshetse | Tripped | July | High | Permanent
2024-07-08 | 06:23 | 089/24 | Francistown | F/Town 11kV Bus Section CB 1SO | 11 | Distribution | North | Clear | 07:49 | 1.43 | SCADA | Tripped; Load loss (7.55 MW) | July | High | Permanent
2024-07-19 | 07:51 | 093/24 | Gab East | Gab East T1A HV CB 110A | 11 | Distribution | South | Clear | 08:37 | 0.77 | SCADA/R. Galetshetse | LV REF trip; Load loss (10 MW) | July | High | Permanent
2024-07-19 | 07:51 | 093/24 | Gab East | Gab East T1A LV CB 1H0A | 11 | Distribution | South | Clear | 08:37 | 0.77 | SCADA/R. Galetshetse | LV REF trip | July | High | Permanent
2024-07-27 | 10:02 | 096/24 | Tlokweng | Tlokweng T1 HV CB 110 | 11 | Distribution | South | Clear | 08:54 | 1.13 | SCADA/Rapelang | REF & Winding trip; Surge arrester blown | July | High | Permanent
2024-07-27 | 10:02 | 096/24 | Tlokweng | Tlokweng T1 LV CB 1HO | 11 | Distribution | South | Clear | 08:54 | 1.13 | SCADA/Rapelang | Tripped | July | High | Permanent
2024-07-27 | 10:02 | 096/24 | Tlokweng | Tlokweng T2 LV CB 2H0 | 11 | Distribution | South | Clear | 11:10 | 1.13 | SCADA/Rapelang | E/F trip; Load loss (8.5 MW) | July | High | Permanent
2024-08-29 | 02:18 | 098/24 | Tlokweng | Tlokweng T1 HV CB 110 | 11 | Distribution | South | Clear | 04:13 | 1.92 | SCADA/Galetshetse | LV Restricted Earth Fault; Through fault from CSS | August | High | Permanent
2024-08-29 | 02:18 | 098/24 | Tlokweng | Tlokweng T1 LV CB 1HO | 11 | Distribution | South | Clear | 04:13 | 1.92 | SCADA/Galetshetse | Tripped | August | High | Permanent
2024-09-04 | 05:58 | 102/24 | Tlokweng | Tlokweng T1 LV CB 1HO | 11 | Distribution | South | Clear | 17:45 | 11.78 | SCADA/Galetshetse | Tripped | September | High | Permanent
2024-09-12 | 07:51 | 103/24 | Jwaneng | Jwaneng T8 LV CB | 6.6 | Distribution | South | Clear | 08:54 | 1.05 | SCADA/Mosarwe | Tripped | September | High | Permanent
2024-09-15 | 08:01 | 105/24 | Zone 5 – Bosetu | T1 LV CB 1T0 | 11 | Distribution | North West | Clear | 12:57 | 4.93 | SCADA/Mosala | Tripped | September | High | Permanent
2024-09-15 | 08:01 | 105/24 | Zone 5 – Bosetu | T2 LV CB 2T0 | 11 | Distribution | North West | Clear | 12:57 | 4.93 | SCADA/Mosala | Tripped | September | High | Permanent
2024-09-20 | 00:56 | 107/24 | Orapa | Orapa 220/33kV T1 LV CB 1H0 | 33 | Distribution | Central | Clear | 11:19 | 50.38 | SCADA/Likokoto | Duplicate of 104/24 | September | High | Permanent
2024-09-28 | 17:41 | 109/24 | WoodHall | WoodHall T1A & T2A LV CBs | 11 | Distribution | South | Cloudy | 20:28 | 2.78 | SCADA/Kaloso | HV O/C trip; Load loss (2.1 MW) | September | High | Permanent
2024-10-11 | 16:21 | 112/24 | Jwaneng | Jwaneng T8 LV CB 8H0 | 33 | Distribution | South | Clear | 17:17 | 0.93 | SCADA | Tripped | October | High | Permanent
2024-10-14 | 19:41 | 112/24 | Francistown West | F/Town West T2A LV CB 1HOA | 11 | Distribution | North | Clear | 21:15 | 1.57 | SCADA/Chabalala | Master trip; Load loss (7.8 MW) | October | High | Permanent
2024-10-16 | 04:18 | 113/24 | G/Enclave | G/Enclave T1 LV CB 1H0 | 11 | Distribution | South | Clear | 05:39 | 1.35 | SCADA/Galetshetse | Phase trip; Bus Section CB also tripped | October | High | Permanent
2024-10-16 | 04:18 | 113/24 | G/Enclave | G/Enclave T2 LV CB 2H0 | 11 | Distribution | South | Clear | 05:39 | 1.35 | SCADA/Galetshetse | Tripped | October | High | Permanent
2024-10-16 | 04:18 | 113/24 | G/Enclave | 11kV Bus Section CB 1SO | 11 | Distribution | South | Clear | 05:39 | 1.35 | SCADA/Galetshetse | Tripped (not updating on SCADA) | October | High | Permanent
2024-11-10 | 23:36 | 137/24 | Gaphatshwa | Gaphatshwa T2 LV CB H20 | 11 | Distribution | South | Clear | 1:03 | 1.45 | SCADA/Galetshetse | Tripped | November | High | Permanent
2024-11-24 | 20:16 | 154/24 | Gaphatshwa | Gaphatshwa T3 LV CB 3H0 | 11 | Distribution | South | Clear | 21:34 | 1.32 | SCADA/Madubeko | Tripped; Load loss (5 MW) | November | High | Permanent
2024-11-24 | 20:16 | 154/24 | Gaphatshwa | Gaphatshwa T4 LV CB 4H0 | 11 | Distribution | South | Clear | 21:35 | 1.32 | SCADA/Madubeko | Tripped | November | High | Permanent
2024-12-01 | 15:38 | 161/24 | S/Phikwe | S/Phikwe 220/11kV Transformer 1 LV CB A2TO | 11 | Distribution | South | Clear | 20:12 | 4.57 | SCADA / Likokotlo | — | December | High | Permanent
2024-12-01 | 15:38 | 161/24 | S/Phikwe | S/Phikwe 220/11kV Transformer 3 LV CB A1TO | 11 | Distribution | South | Clear | 20:12 | 4.57 | SCADA / Likokotlo | — | December | High | Permanent
2024-12-06 | 02:18 | 163/24 | S/Phikwe | S/Phikwe 220/11kV Transformer 3 LV CB A1TO | 11 | Distribution | Central | Clear | 07:43 | 5.42 | SCADA / Boiditswe | 11kV Inter trip send, Master trip | December | High | Permanent
2024-12-10 | 22:33 | 166/24 | Maun | Maun 132/11kV T2 HV & LV CBs 210 & 2TO | 11 | Distribution | North/West | Clear | 23:57 | 1.37 | SCADA / Rasefako | Earth fault & Master trip; Loss of supply to Maun and surrounding areas | December | High | Permanent
2024-12-14 | 15:52 | 169/24 | Woodhall | Woodhall T1A 11kV CB 1HO | 11 | Distribution | South | Rainy | 16:40 | 0.8 | SCADA / Galetshetse | HV O/C Low set trip & I/T Rec; Load loss to Lobatse (2.2 MW) | December | High | Permanent
2024-12-14 | 15:52 | 169/24 | Woodhall | Woodhall T2A 11kV CB 2HO | 11 | Distribution | South | Rainy | 17:02 | 1.17 | SCADA / Galetshetse | TX protection trip & 11kV I/T Rec | December | High | Permanent
2024-12-31 | 18:15 | 188/24 | Woodhall | Woodhall T1A: 11kV CB 1H0 | 11 | Distribution | South | Rainy | 18:59 | 0.73 | SCADA / Charles | BUS ZONE, TRIP ZONE1, CB FAIL TRIP | December | High | Permanent
2024-12-31 | 18:15 | 188/24 | Woodhall | Woodhall T4: 33kV CB H40 | 33 | Distribution | South | Rainy | 19:11 | 0.92 | SCADA | — | December | High | Permanent
2025-01-26 | 05:37 | 020.1/25 | Woodhall | Woodhall T1A LV CB 1H0 | 11 | Distribution | South | Clear | 07:46 | 2.15 | SCADA / Galetshetse | HV O/C Low set & Standby E/F High set; CSS reported fallen 11kV conductors; Load loss 1.8 MW | January | High | Permanent
2025-02-10 | 09:22 | 067/25 | Tlokweng | Tlokweng 132/11kV T2 LV CB 2H0 | 11 | Distribution | Tlokweng | Cloudy | 18:33 | 9.18 | SCADA / Galetshetse | — | February | High | Permanent
2025-02-19 | 12:26 | 061/25 | Gaphwatshwa | Gaphwatshwa 132/33kV T2 LV CB H20 | 33 | Distribution | South | Rain | 13:03 | 0.45 | SCADA / Kaloso | LV O/C & E/F trip; Master trip | February | Medium | Sustained
2025-02-19 | 12:40 | 062/25 | Broadhurst | Broadhurst 132/33kV LV CB 4T0 | 33 | Distribution | South | Rain | 13:03 | 0.45 | SCADA / Kaloso | LV O/C & E/F trip; Master trip | February | Medium | Sustained
2025-02-28 | 11:20 | 072/25 | Mogoditshane | Mogoditshane 132/11kV T4 LV CB 4HO | 11 | Distribution | South | Clear | 12:30 | 1.17 | SCADA / A. Mangole | — | February | High | Permanent
2025-03-02 | 7:58 | 075/25 | Kanye | Kanye 132/11kV Tx 2 LV CB 2HO | 11 | Distribution | South | Rainy | 2:11 | 18.22 | SCADA / Baikgantshi | 3Ph T + L/O | March | High | Permanent
2025-03-09 | 18:30 | 077/25 | Government Enclave, 132/11kV T1 | Government Enclave 132/11kV T1 LV CB 1HO | 11 | Distribution | South | Clear | 19:55 | 1.42 | SCADA | Tripped | March | High | Permanent
2025-03-13 | 4:46 | 084/25 | F/Town West | F/Town West 132/11kV Tx 2A LV CB 2HOB | 11 | Distribution | North | Cloudy | 5:43 | 0.95 | SCADA / Chabalala | LV OC & EF Relay: Trip. LV master trip operated | March | High | Permanent
2025-03-13 | 6:23 | 084/25 | F/Town West | F/Town West 132/11kV Tx 2A LV CB 2HOB | 11 | Distribution | North | Cloudy | 7:04 | 0.68 | SCADA / Chabalala | LV OC & EF Relay: Trip. LV master trip operated | March | High | Permanent
2025-03-13 | 13:01 | 078/25 | Francistown | Francistown 220/11kV TX 1B LV CB 1TOB | 11 | Distribution | North | Cloudy | 14:12 | 1.18 | SCADA / Magola | F/town, 220/11kV TX 1B LV side; Ground to neutral, O/C trip | March | High | Permanent
2025-03-13 | 13:01 | 078/25 | Francistown | Francistown 220/11kV TX 1A LV CB 1TOA | 11 | Distribution | North | Cloudy | 17:13 | 4.2 | SCADA / Magola | F/town, 220/11kV TX 1A LV side; Backup protection trip | March | High | Permanent
2025-03-22 | 15:05 | 88/25 | Orapa 2 | Orapa 2 220/33kV T1 LV CB H08 | 33 | Distribution | Central | Clear | 16:18 | 1.22 | SCADA | LoStage E/F operated; Letlhakane Village feeder OHL conductor broken | March | High | Permanent
2025-03-28 | 19:59 | 091/25 | Gaphatshwa | Gaphatshwa 132/11kV Transformer 4 LV CB 4HO | 11 | Distribution | South | Normal | 21:55 | 1.93 | SCADA | Over voltage, Master trip operated | March | High | Permanent
2025-03-28 | 19:59 | 091/25 | Gaphatshwa | Gaphatshwa 132/11kV Transformer 3 LV CB 3HO | 11 | Distribution | South | Normal | 21:55 | 1.93 | SCADA | Over voltage, Master trip operated | March | High | Permanent
2025-04-09 | 6:46 | 095/25 | Jwaneng | Jwaneng 132/33kV Transformer 9 LV CB 9HO | 33 | Distribution | South | Rainy | 16:03 | 9.28 | SCADA / Mosarwe | Through fault from CSS Feeder 4L5 (failed to trip); restored after isolation | April | High | Permanent
2025-04-12 | 10:53 | 097/25 | Jwaneng | Jwaneng 132/33kV Transformer 9 LV CB 9HO | 33 | Distribution | South | Cloudy | 11:31 | 0.63 | SCADA / Mosarwe | Buszone trip; Mine Feeder 5 tripped on O/C, E/F | April | High | Permanent
2025-04-12 | 14:24 | 098/25 | Jwaneng | Jwaneng 132/33kV Transformer 9 LV CB 9HO | 33 | Distribution | South | Cloudy | 14:51 | 0.45 | SCADA / Mosarwe | Buszone trip; Mine Feeder 5 tripped on O/C, E/F | April | Medium | Sustained
2025-04-19 | 9:27 | 099/25 | Broadhurst | Broadhurst 132/11kV TRF 1 LV CB 3H0 | 11 | Distribution | South | Cloudy | 14:05 | 4.63 | SCADA / R. Galetshetse | Overcurrent trip; Zone 2 trip, underfrequency relay | April | High | Permanent
2025-04-19 | 9:27 | 099/25 | Broadhurst | Broadhurst 132/11kV TRF 2 LV CB 4HO | 11 | Distribution | South | Cloudy | 11:51 | 50.4 | SCADA / R. Galetshetse | Underfrequency relay trip | April | High | Permanent
2025-04-23 | 22:13 | 102/25 | Mochudi | Mochudi 132/33kV Transformer 1 LV CB 110 | 33 | Distribution | South | Clear | 0:29 | 2.27 | SCADA / E. Ntoko | Earth fault | April | High | Permanent
2025-04-30 | 7:15 | 103/25 | Jwaneng | Jwaneng 132/33kV Tx 9 LV CB 9HO | 33 | Distribution | South | Sunny | 8:03 | 0.8 | SCADA / Mosarwe | E/F trip | April | High | Permanent
2025-04-30 | 9:12 | 104/25 | Jwaneng | Jwaneng 132/33kV Tx 8 LV CB 8HO | 33 | Distribution | South | Sunny | 9:34 | 0.37 | SCADA / Mosarwe / Charles | Buszone trip; baboons seen in substation, flash on 33kV busbar | April | Medium | Sustained
2025-05-03 | 10:20 | 108/25 | Maun | Maun 132/11kV Transformer 1 LV CB 1T0 | 11 | Distribution | North | Sunny | 16:13 | 5.88 | SCADA / Magola | Protection Trip, Current Relay operated | May | High | Permanent
2025-05-03 | 10:20 | 108/25 | Maun | Maun 11kV Bus Section CB 1S0 | 11 | Distribution | North | Sunny | 16:19 | 5.98 | SCADA / Magola | Protection Trip | May | High | Permanent
2025-05-23 | 22:13 | 102/25 | Mochudi | Mochudi 132/33kV Transformer 1 LV CB 110 | 33 | Distribution | South | Clear | 0:29 | 2.27 | SCADA / E. Ntoko | Earth fault | May | High | Permanent
2025-06-08 | 11:52 | 123/25 | Phakalane | Phakalane 132/11kV Transformer 2 LV CB 2HOB | 11 | Distribution | South | Clear | 12:31 | 0.65 | SCADA | Inter trip receive | June | High | Permanent
2025-06-08 | 11:52 | 123/25 | Phakalane | Phakalane 11kV Bussection CB 1SOB | 11 | Distribution | South | Clear | 12:31 | 0.65 | SCADA | CB FAIL Right hand side | June | High | Permanent
2025-06-25 | 17:31 | 128/25 | Molepolole | Molepolole 132/33kV T1 LV CB H10 | 33 | Distribution | South | Clear | 20:48 | 3.28 | Kgame/Galetshetse | LV Directional E/F Trip | June | High | Permanent