## Monthly_Fault_Data__Jan_Mar1
Date | Trip Time | Fault No | Location (Town) | Apparatus Tripped | Voltage Level(KV) | System Type | Substation Area | Weather | Time Reclosed | Downtime (Hours) | Reported By | Comments | Month | Severity | Fault type
2023-06-01 | 08:09 | 004/23 | Jwaneng | Jwaneng 132/33 T8: LV CB 8HO | 33 | Distribution | South | Clear | 08:51 | 0.7 | SCADA/Mosarwe | Bus zone trip | January | High | Permanent
2023-06-01 | 15:33 | 005/23 | Orapa | Orapa1 220/33 Transformer 2: LV CB H10 | 33 | Distribution | North | Rainy | 16:30 | 0.95 | SCADA/Theophilus | LV O/C trip, Winding Temp Trip & Oil Temp Alarm | January | High | Permanent
2023-07-01 | 11:35 | 007/23 | Sua Pan | Sua Pan 132/11 CBs 3L5 & 4L5 | 11 | Distribution | North | Clear | 19:56 | 8.35 | SCADA | Overcurrent protection, smoke on 11 busbar, Botash not importing | January | High | Permanent
17/01/2023 | 18:46 | 113/23 | Woodhall | Woodhall 132/11 Transformer 1A: LV CB 1HO | 11 | Distribution | Central | Cloudy | 23:29 | 4.717 | SCADA/Ramacha |  | January | High | Permanent
29/01/2023 | 22:38 | 016/23 | Orapa | Orapa 1 220/33 Transformer 2: LV CB H10 | 33 | Distribution | Central | Rainy | 23:25 | 0.85 | SCADA/MMUSI | 33 OVERVOLTAGE TRIP, Winding Temp Alarm & Trip Low set, Master trip | January | High | Permanent
2023-09-02 | 15:53 | 036/23 | Orapa | Orapa 2 GEN Tx 1: LV CB 01BAT10 | 11 | Distribution | North | Clear | 16:45 | 1.2 | SCADA/Batleng | DIFF protection operated | February | High | Permanent
17/02/2023 | 23:31 | 051/23 | Fancistown West | FWST 132/11 T1A & T2A: 11 CBs 1HOA & 2HOA | 11 | Distribution | North | Cloudy | 00:20 | 0.817 | SCADA/Serema | Earth Fault (E/F) protection trip | February | High | Permanent
18/02/2023 | 01:40 | 052/23 | Fancistown West | FWST 132/11 T1A & T2A: 11 CBs 1HOA & 2HOA | 11 | Distribution | North | Cloudy | 02:44 | 1.4 | SCADA/Serema | Earth Fault (E/F) protection trip recurrence | February | High | Permanent
14/03/2023 | 13:52 | 078/23 | Boteti | BDHT 132/11 Transformer 3 & Bus Section | 11 | Distribution | Central | Rainy | 14:36 | 0.73 | SCADA/Boteti | Buchholz trip, Oil surge, internal fault suspected | March | High | Permanent
15/03/2023 | 17:52 | 087/23 | Tlokweng | Tlokweng 132/11 Transformer 1: LV CB 1HO | 11 | Distribution | South | Clear | 18:40 | 0.8 | SCADA/Tlokweng | O/C trip, Master trip | March | High | Permanent
31/03/2023 | 06:02 | 096/23 | Woodhall | Woodhall 132/33 TRF 3: HV CB 310 & LV CB H30 | 33 | Distribution | South | Cloudy | ARC | 0 | SCADA | No time reclosed likely no restoration indication; breaker sequence: Tripped | March | Low | Transient
18/04/2022 | 3:26 | 117/23 | Kanye | Kanye 132/11 kV Transformer 1: LV CB 1HO | 11 | Distribution | South | Clear | 5:42 | 1.27 | SCADA/Baoki | Trip was due to a through fault from feeder 4L5. | April | High | Permanent
18/04/2022 | 3:26 | 117/23 | Kanye | Kanye 132/11 kV Transformer 2: LV CB 2H0 | 11 | Distribution | South | Clear | 5:42 | 1.27 | SCADA/Baoki | Trip was due to a through fault from feeder 4L5. | April | High | Permanent
18/04/2022 | 7:35 | 118/23 | Kanye | Kanye 132/11 kV Transformer 1: LV CB 1HO | 11 | Distribution | South | Clear | 8:19 | 0.73 | SCADA/Baoki | Trip was due to a through fault from feeder 4L5. Further patrolling carried out. | April | High | Permanent
18/04/2022 | 7:35 | 118/23 | Kanye | Kanye 132/11 kV Transformer 2: LV CB 2H0 | 11 | Distribution | South | Clear | 8:19 | 0.73 | SCADA/Baoki | Trip was due to a through fault from feeder 4L5. Further patrolling carried out. | April | High | Permanent
2023-07-04 | 8:07 | 105/23 | BDHT | BDHT 132/11kV Transformer 1 | 11 | Distribution | South | Clear | 9:02 | 0.95 | SCADA / Ntoko |  | April | High | Permanent
2023-07-04 | 8:07 | 105/23 | BDHT | BDHT 132/11kV Transformer 4 | 11 | Distribution | South | Clear | 9:00 | 0.92 | SCADA |  | April | High | Permanent
2023-07-04 | 8:07 | 105/23 | MOGS | MOGS 132/33kV Transformer 1 | 33 | Distribution | South | Clear | 9:01 | 0.93 | SCADA |  | April | High | Permanent
2023-07-04 | 8:07 | 105/23 | MOGS | MOGS 132/33kV Transformer 2 | 33 | Distribution | South | Clear | 9:01 | 0.93 | SCADA |  | April | High | Permanent
2023-11-04 | 3:17 | 111/23 | MORP | Morp A Generator 2 12kv CB 2GO | 12 | Distribution | Central | Clear | 10:51 | 7.57 | SCADA / Ralesota | Load loss: 20 MW, 151.3 MWh | April | High | Permanent
26/04/2023 | 17:19 | 121/23 | Jwaneng | Jwaneng 132/33kV Transformer 9 HV CB 410 | 33 | Distribution | South | Clear | 18:02 | 0.72 | SCADA / Mosarwe | Load loss to Debswana Mine Boreholes power supply. | April | High | Permanent
26/04/2023 | 17:19 | 121/23 | Jwaneng | Jwaneng 132/33kV Transformer 9 LV CB 9H0 | 33 | Distribution | South | Clear | 18:02 | 0.72 | SCADA / Mosarwe | Load loss to Debswana Mine Boreholes power supply. | April | High | Permanent
2023-05-05 | 15:15 | 124/23 | B/HURST | B/HURST 132/11kV Transformer 2 LV CB 4H0 | 11 | Distribution | South | Clear | 17:05 | 1.83 | SCADA/MAKOKO | Intertrip Receive/Send; Tripped | May | High | Permanent
2023-05-05 | 15:15 | 124/23 | MOGS | MOGS 132/11kV Transformer 3 HV CB 410 | 11 | Distribution | South | Clear | 17:08 | 1.88 | SCADA | Intertrip Receive; Tripped | May | High | Permanent
2023-05-05 | 15:15 | 124/23 | MOGS | MOGS 132/11kV Transformer 3 LV CB 3H0 | 11 | Distribution | South | Clear | 17:13 | 1.97 | SCADA | Tripped | May | High | Permanent
2023-05-05 | 15:15 | 124/23 | MOGS | MOGS 132/11kV Transformer 4 HV CB 510 | 11 | Distribution | South | Clear | 17:08 | 1.88 | SCADA | Intertrip Receive; Tripped | May | High | Permanent
2023-05-05 | 15:15 | 124/23 | MOGS | MOGS 132/11kV Transformer 4 LV CB 4H0 | 11 | Distribution | South | Clear | 17:13 | 1.97 | SCADA | Tripped | May | High | Permanent
2023-08-05 | 0:16 | 128/23 | Mowana | Mowana 132/11kV Transformer 1 | 11 | Distribution | IPS | Clear | 5:22 | 5.1 | SCADA | Overvoltage; Tripped | May | High | Permanent
2023-08-05 | 0:13 | 128/23 | Orapa | Orapa 2 220/33kV Transformer 1 HV CB H10 | 33 | Distribution | IPS | Clear | 5:41 | 5.47 | SCADA | Overvoltage; Tripped | May | High | Permanent
31/05/2023 | 5:14 | 140/23 | Gov/Enclave | Gov/Enclave 132/11kV TRF 2 HV CB 280 | 11 | Distribution | South | Cloudy | 15:03 | 9.82 | SCADA/Ntoko | Master Trip Operated; Tap Change Buchholz Operated | May | High | Permanent
31/05/2023 | 5:14 | 140/23 | Gov/Enclave | Gov/Enclave 132/11kV TRF 2 LV CB 2HO | 11 | Distribution | South | Cloudy | 15:03 | 9.82 | SCADA/Ntoko | Under Frequency; Protection Trip | May | High | Permanent
2023-02-06 | 10:48 | 141/23 | Maun | Maun 132/11kV Transformer 1 HV CB 110 | 11 | Distribution | North | Clear | 11:25 | 0.62 | SCADA/MOSALA | Did not trip initially; High set O/C on Matshwane feeder; later tripped | June | High | Permanent
2023-02-06 | 10:48 | 141/23 | Maun | Maun 132/11kV Transformer 2 LV CB 2TO | 11 | Distribution | North | Clear | 11:25 | 0.62 | SCADA/MOSALA | O/C trip | June | High | Permanent
15/06/2023 | 15:18 | 147/23 | Makoba | Makoba 132/33kV T2 HV & LV CBs 210 & T20 | 33 | Distribution | North West | Clear | 15:40 | 0.37 | SCADA/Chabalala | LV Bus zone 2 trip & Mastertrip operated | June | Medium | Sustained
15/06/2023 | 15:18 | 147/23 | Makoba | 33kV Bus Bar B/S CB S10 | 33 | Distribution | North West | Clear | 15:40 | 0.37 | SCADA/Chabalala | Zone 2 trip, Check Zine trip & Zone 2 trip L1 | June | Medium | Sustained
29/06/2023 | 2:28 | 154/23 | Motheo Mine | Motheo Mine 11kV B/Section CB 1SO | 11 | Distribution | North West | Clear | 4:07 | 1.65 | Scada/CSS | No indication; Tripped | June | High | Permanent
08/08/2023 | 03:35 | 150/23 | Morupule A | Morupule A Generator 3 11kV CB 3G0 | 11 | Distribution | Central | Clear | TBA | 0 | SCADA | Thermal Stress; Tripped | August | Low | Transient
23/09/2023 | 21:26 | 162/23 | Kgale View | Kgale View T1 & T2 11kV LV CB 1H0 | 11 | Distribution | South | Clear | 00:24 | 2.97 | Scada / Galetshetse | Arc protection; TRIP | September | High | Permanent
23/09/2023 | 21:26 | 162/23 | Kgale View | Kgale View T1 & T2 11kV LV CB 2H0 | 11 | Distribution | South | Clear | 23:03 | 1.62 | SCADA/Galetshetse | Arc protection; TRIP | September | High | Permanent
23/09/2023 | 21:26 | 162/23 | Kgale View | Kgale View B/section CB 1SO | 11 | Distribution | South | Clear | 00:24 | 2.97 | SCADA/Galetshetse | Arc protection; TRIP | September | High | Permanent
24/09/2023 | 06:08 | 163/23 | Karowe | Karowe T1 LV CB 1T0 | 11 | Distribution | North | Clear |  | 0 | SCADA/Phillip | TRIP (No load loss as B/Section CB 1SO was closed) | September | Low | Transient
28/09/2023 | 18:55 | 164/23 | Phakalane | Phakalane T1B LV CB 1HOB | 11 | Distribution | South | Clear | 19:00 | 0.08 | SCADA/Selei | Buchholz Alarm; TRIP | September | Low | Transient
05/10/2023 | 12:37 | 168/23 | BDHT | BDHT 132/11kV Transformer 1 | 11 | Distribution | South | Clear | 13:15 | 0.63 | SCADA / Ntoko | Zone 1,2,3 Trip, Master Trip, Underfreq | October | High | Permanent
17/11/2023 |  | 191/23 | Gab East | Gab East 132/11kV T2B LV CB 2HOB | 11 | Distribution | South | Clear | 07:58 | 1.95 | SCADA / Ntoko | Trip | November | High | Permanent
17/11/2023 |  | 191/23 | Gab East | 11kV Bussection CB 1SOB | 11 | Distribution | South | Clear | 08:15 | 2.18 | SCADA / Ntoko | Master trip, Buszone trip, Trip Circuit Supervision 1 | November | High | Permanent
18/11/2023 |  | 192/23 | Gab East | Gab East 132/11kV T1B LV CB 1HOB | 11 | Distribution | South | Clear | 02:57 | 2.27 | SCADA / Ntoko | Buszone operated, VT Fail | November | High | Permanent
18/11/2023 |  | 192/23 | Gab East | Gab East 132/11kV T2B LV CB 2HOB | 11 | Distribution | South | Clear | 02:58 | 2.28 | SCADA / Ntoko | Tripped | November | High | Permanent
18/11/2023 |  | 192/23 | Gab East | Gab East 132/11kV T3B LV CB 3HOB | 11 | Distribution | South | Clear | 02:58 | 2.28 | SCADA / Ntoko | Tripped | November | High | Permanent
18/11/2023 |  | 192/23 | Gab East | Gab East 11kV CB 1SOB | 11 | Distribution | South | Clear | 02:58 | 2.28 |  | Phase A & B trip, Buszone Phase B and C | November | High | Permanent
12/12/2023 | 17:51 | 206/23 | Morupule A | Morp.A Unit 2 12kV CB 2GO | 12 | Distribution | Central | Clear | TBA | 0 | SCADA | Flame failure; TRIPPED | December | Low | Transient
15/12/2023 | 17:06 | 206/23 | Hydromet | Hydromet 66/33kV TRF 01 HV CB H10 | 33 | Distribution | North | Clear | 18:54 | 1.8 | Scada/Kahona/Chabalala | Tertiary E/Fault, Master Trip; TRIPPED | December | High | Permanent
15/12/2023 |  | 206/23 | Hydromet | Hydromet 66/33kV TRF 01 LV CB 180 | 33 | Distribution | North | Clear | 18:54 | 1.8 | Scada/Kahona/Chabalala | Tertiary E/Fault, Master Trip; TRIPPED | December | High | Permanent
15/12/2023 |  | 206/23 | Hydromet | 33kV Bus Coupler CB 130 | 33 | Distribution | North | Clear | 18:04 | 0.97 | SCADA/Kahona | Closed to restore supply via TX 03 | December | High | Permanent
23/12/2023 | 14:38 | 211/23 | Morupule A | Morp.A Unit 1 12kV CB 1GO | 12 | Distribution | Central | Clear | TBA | 0 | SCADA | Furnace pressure high; TRIPPED | December | Low | Transient
25/12/2023 | 09:50 | 211/23 | Orapa 1 | Orapa 1 220/33 kV Tx 3: HV CB H30 | 33 | Distribution | Central | Rainy | 13:58 | 4.13 | SCADA/Likokoto | Tap changer overpressure trip; Water ingress found on overpressure termination box | December | High | Permanent
27/12/2023 | 00:39 | 213/23 | Morupule A | Morupule A 12kV CB 3GO | 12 | Distribution | Central | Cloudy | 05:05 | 4.43 | Obed | Generator temperature high; Tripped | December | High | Permanent
04/01/2024 | 02:10 | 005/24 | Gaphatshwa | 132/11kV T3 CB 3H0 | 11 | Distribution | South | Clear | 03:51 | 1.68 | SCADA/Ntoko | TRIP | January | High | Permanent
04/01/2024 | 05:23 | 005/24 | Gaphatshwa | 132/11kV T4 CB 4H0 | 11 | Distribution | South | Clear | 03:51 | 1.68 | SCADA/Ntoko | TRIP | January | High | Permanent
07/01/2024 | 11:52 | 008/24 | F/Town West | F/Town West 132/11kV Transformer 1 : LV CB 1HOA | 11 | Distribution | North | Clear | 12:53 | 1.02 | SCADA/Chabalala | master trip, High set O/C, On Bus Section CB - High set O/C; Tripped | January | High | Permanent
07/01/2024 | 11:52 | 008/24 | F/Town West | 11kV B/Section : CB 1S0A | 11 | Distribution | North | Clear | 12:53 | 1.02 | SCADA/Chabalala | Tripped | January | High | Permanent
15/01/2024 | 22:15 | 019/24 | Ghanzi | Ghanzi 132/11kV T1 LV CB 1H0 | 11 | Distribution | South | Cloudy | 3:43 | 5.47 | Rasefako | Phase B-C O/C protetction; Tripped | January | High | Permanent
15/01/2024 | 22:15 | 019/24 | Ghanzi | Ghanzi 132/11kV T2 LV CB 2H0 | 11 | Distribution | South | Cloudy | 3:43 | 5.47 | Rasefako | Phase B-C O/C protetction; Tripped | January | High | Permanent
16/01/2024 | 10:00 | 023/24 | Ramotswa | Ramotswa 132/11kV T3 HV CB 310 | 11 | Distribution | South | Clear | 10:27 | 0.45 | SCADA/Ntoko | Zone 1,2,3 Trip, Master Trip, Underfreq; Tripped | January | Medium | Sustained
16/01/2024 | 10:00 | 023/24 | Ramotswa | Ramotswa 132/11kV T3 LV CB 3H0 | 11 | Distribution | South | Clear | 10:27 | 0.45 | SCADA/Ntoko | Zone 1,2,3 Trip, Master Trip, Underfreq; Tripped | January | Medium | Sustained
26/01/2024 | 08:34 | 028/24 | Jwaneng | Jwaneng 132/33 kV Transformer 8: LV CB 8H0 | 33 | Distribution | South | Clear | 09:04 | 0.5 | SCADA / Baikgantshi | 33kV bus zone: R-ɸ start, 89 alarm, 87 DIFF start, breaker fail, W-ɸ start, B-ɸ trip, zone 1 trip; Tripped | January | Medium | Sustained
26/01/2024 | 08:34 | 028/24 | Jwaneng | 33kV Cap Bank 2 CB 4L5 | 33 | Distribution | South | Clear | 09:17 | 0.72 | SCADA / Baikgantshi | Tripped | January | High | Permanent
26/01/2024 |  | 028/24 | Jwaneng | Jwaneng 132/33 kV Transformer 8: HV CB 110 | 33 | Distribution | South | Clear |  | 0 | SCADA / Baikgantshi | Did not trip | January | Low | Transient
26/01/2024 | 12:38 | 029/24 | Gab East | Gab EAST 132/11 kV Transformer 2B: HV CB 210B | 11 | Distribution | South | Clear | 13:15 | 0.62 | SCADA / Makoko | Did not trip initially; Tripped | January | High | Permanent
26/01/2024 | 12:38 | 029/24 | Gab East | LV CB 2H0B | 11 | Distribution | South | Clear | 13:16 | 0.63 | SCADA / Makoko | Instateneous trip; Tripped | January | High | Permanent
26/01/2024 | 12:38 | 029/24 | Gab East | 11 kV Bus Section CB 1S0B | 11 | Distribution | South | Clear | 13:18 | 0.67 | SCADA / Makoko | L/H bus zone 3ɸ trip, Centre zone trip, bus zone A & B trip; Tripped | January | High | Permanent
2024-02-07 | 17:59 | 041/24 | Ghanzi | Ghanzi Tx 1 LV CB 1H0 | 11 | Distribution | NW | Clear | 18:44 | 0.75 | SCADA | O/C trip; Through fault from feeder 2L5 | February | High | Permanent
2024-02-07 | 17:59 | 041/24 | Ghanzi | Ghanzi Tx 2 LV CB 2H0 | 11 | Distribution | NW | Clear | 18:44 | 0.75 | SCADA | O/C trip | February | High | Permanent
2024-02-11 | 10:03 | 046/24 | GAB EAST | Tx 2B HV CB 210B | 11 | Distribution | South | Clear | 10:42 | 0.65 | SCADA/Makoko | Tripped | February | High | Permanent
2024-02-11 | 11:00 | 046/24 | GAB EAST | Tx 2B LV CB 2H0B | 11 | Distribution | South | Clear | 11:29 | 0.48 | SCADA/Makoko | Tripped again during restoration | February | Medium | Sustained
2024-02-11 | 11:00 | 046/24 | GAB EAST | 11kV Bus Section CB 2S0B | 11 | Distribution | South | Clear | 11:29 | 0.48 | SCADA/Makoko | Phase A–C trip, bus zone trip | February | Medium | Sustained
2024-02-17 | 21:02 | 049/24 | Gaphatshwa | Gaphatshwa T4 11kV CB 4HO | 11 | Distribution | South | Clear | 22:21 | 1.32 | E. NTOKO/SCADA | Overvoltage trip; Feeder 10L5 conductor down | February | High | Permanent
2024-02-26 | 07:07 | 037/24 | Mmakgodumo | Mmakgodumo T1 LV CB H10 | 33 | Distribution | South | Clear | 09:52 | 2.75 | SCADA/Baoki | OC & E/F Phase B&C; Load loss (4 MW) | February | High | Permanent
2024-02-26 | 07:07 | 037/24 | Mmakgodumo | Mmakgodumo T2 LV CB H20 | 33 | Distribution | South | Clear | 11:37 | 4.5 | SCADA/Baoki | OC & E/F Phase B&C; Load loss (4 MW) | February | High | Permanent
2024-03-16 | 21:08 | 058.3/24 | Tlokweng | Tlokweng T1 HV & LV CBs 110 & 1H0 | 11 | Distribution | South | Clear | 00:37 | 3.48 | SCADA/Mangole | Under voltage trip | March | High | Permanent
2024-03-16 | 21:08 | 058.3/24 | Tlokweng | Tlokweng T2 HV & LV CBs 210 & 2H0 | 11 | Distribution | South | Clear | 00:37 | 3.48 | SCADA/Mangole | Under voltage trip | March | High | Permanent
2024-03-16 | 21:08 | 058.3/24 | Gaphatshwa | Gaphatshwa T3 & T4 HV CBs 410 & 210; LV CBs 3H0 & 4H0 | 11 | Distribution | South | Clear | 01:35 | 4.45 | SCADA/Makoko | Low set E/F trip | March | High | Permanent
2024-03-30 | 17:05 | 062/24 | Kanye | Kanye T1 LV CB 1HO | 11 | Distribution | South | Clear | 21:22 | 4.28 | SCADA/Mosarwe/Baoki | OC & E/F trip; Load loss (5.8 MW) | March | High | Permanent
2024-03-30 | 17:05 | 062/24 | Kanye | Kanye T1 HV CB 180 | 11 | Distribution | South | Clear | NIL | 0 | SCADA/Mosarwe/Baoki | DID NOT TRIP | March | Low | Transient
2024-03-30 | 17:05 | 062/24 | Kanye | Kanye T2 LV CB 2HO | 11 | Distribution | South | Clear | 17:50 | 0.75 | SCADA/Mosarwe/Baoki | OC & E/F trip | March | High | Permanent
2024-03-30 | 17:05 | 062/24 | Kanye | Kanye T2 HV CB 280 | 11 | Distribution | South | Clear | NIL | 0 | SCADA/Mosarwe/Baoki | DID NOT TRIP | March | Low | Transient
2024-03-16 | 21:08 | 058.3/24 | Tlokweng | Tlokweng T1 HV & LV CBs 110 & 1H0 | 11 | Distribution | South | Clear | 00:37 | 3.48 | SCADA/Mangole | Under voltage trip | March | High | Permanent
2024-03-16 | 21:08 | 058.3/24 | Tlokweng | Tlokweng T2 HV & LV CBs 210 & 2H0 | 11 | Distribution | South | Clear | 00:37 | 3.48 | SCADA/Mangole | Under voltage trip | March | High | Permanent
2024-03-16 | 21:08 | 058.3/24 | Gaphatshwa | Gaphatshwa T3 & T4 HV CBs 410 & 210; LV CBs 3H0 & 4H0 | 11 | Distribution | South | Clear | 01:35 | 4.45 | SCADA/Makoko | Low set E/F trip | March | High | Permanent
2024-03-30 | 17:05 | 062/24 | Kanye | Kanye T1 LV CB 1HO | 11 | Distribution | South | Clear | 21:22 | 4.28 | SCADA/Mosarwe/Baoki | OC & E/F trip; Load loss (5.8 MW) | March | High | Permanent
2024-03-30 | 17:05 | 062/24 | Kanye | Kanye T1 HV CB 180 | 11 | Distribution | South | Clear | NIL | 0 | SCADA/Mosarwe/Baoki | DID NOT TRIP | March | Low | Transient
2024-03-30 | 17:05 | 062/24 | Kanye | Kanye T2 LV CB 2HO | 11 | Distribution | South | Clear | 17:50 | 0.75 | SCADA/Mosarwe/Baoki | OC & E/F trip | March | High | Permanent
2024-03-30 | 17:05 | 062/24 | Kanye | Kanye T2 HV CB 280 | 11 | Distribution | South | Clear | NIL | 0 | SCADA/Mosarwe/Baoki | DID NOT TRIP | March | Low | Transient
2024-05-04 | 04:23 | 071/24 | Mogoditshane | Mogoditshane T3 HV CB 410 | 11 | Distribution | South | Clear | 2:42 | 1.68 | SCADA/Galetshetse | Tripped; Load loss (6 MW) | May | High | Permanent
2024-05-04 | 04:23 | 071/24 | Mogoditshane | Mogoditshane T3 LV CB 3H0 | 11 | Distribution | South | Clear | 2:42 | 1.68 | SCADA/Galetshetse | Tripped | May | High | Permanent
2024-05-04 | 04:23 | 071/24 | Mogoditshane | Mogoditshane T4 HV CB 510 | 11 | Distribution | South | Clear | 2:42 | 1.68 | SCADA/Galetshetse | Tripped | May | High | Permanent
2024-05-04 | 04:23 | 071/24 | Mogoditshane | Mogoditshane T4 LV CB 4H0 | 11 | Distribution | South | Clear | 2:42 | 1.68 | SCADA/Galetshetse | Tripped | May | High | Permanent
2024-05-24 | 20:36 | 077/24 | Francistown West | F/Town West T1A LV CB 1HOA | 11 | Distribution | North | Clear | 22:31 | 1.92 | SCADA/Makoko | Tripped; Load loss (8.7 MW) | May | High | Permanent
2024-05-24 | 20:36 | 077/24 | Francistown West | F/Town West T2A LV CB 2HOA | 11 | Distribution | North | Clear | 22:33 | 1.95 | SCADA/Makoko | Tripped | May | High | Permanent
2024-05-31 | 07:51 | 079/24 | Gab East | Gab East T1A HV CB 110A | 11 | Distribution | South | Clear | 08:37 | 0.77 | SCADA/R. Galetshetse | LV REF trip; Load loss (10 MW) | May | High | Permanent
2024-05-31 | 15:35 | 079/24 | Orapa | Orapa 2 T1 HV CB H10 | 33 | Distribution | North | Clear | 18:46 | 3.18 | SCADA/Maduo | Master trip; Load loss (15 MW) | May | High | Permanent
2024-05-31 | 15:35 | 079/24 | Orapa | Orapa 2 T1 LV CB H08 | 33 | Distribution | North | Clear | 18:50 | 3.25 | SCADA/Louis | E/F trip | May | High | Permanent
2024-06-01 | 16:50 | 080/24 | Woodhall | Woodhall T3 LV CB H30 | 33 | Distribution | North | Clear | ARC | 0 | SCADA/Ramacha | LV CB Close block | June | Low | Transient
2024-06-04 | 05:07 | 082/24 | Lobatse | Lobatse T2A HV CB 210 | 11 | Distribution | South | Clear | 03:41 | 1.43 | SCADA/Ramacha | Tripped; Load loss | June | High | Permanent
2024-06-04 | 05:07 | 082/24 | Lobatse | Lobatse T2A LV CB 2H0 | 11 | Distribution | South | Clear | 03:41 | 1.43 | SCADA/Ramacha | Tripped | June | High | Permanent
2024-06-07 | 07:51 | 082/24 | Gab East | Gab East T1A HV CB 110A | 11 | Distribution | South | Clear | 08:37 | 0.77 | SCADA/R. Galetshetse | LV REF trip; Load loss (10 MW) | June | High | Permanent
2024-06-07 | 07:51 | 082/24 | Gab East | Gab East T1A LV CB 1H0A | 11 | Distribution | South | Clear | 08:37 | 0.77 | SCADA/R. Galetshetse | LV REF trip | June | High | Permanent
2024-06-17 | 09:41 | 083/24 | Maun | Maun T1 LV CB 1T0 | 11 | Distribution | North | Clear | 11:08 | 1.45 | SCADA/Sekgatlhola | Tripped | June | High | Permanent
2024-06-17 | 09:45 | 083/24 | Maun | Maun T2 HV CB 210 | 11 | Distribution | North | Clear | 10:59 | 1.23 | SCADA/Sekgatlhola | Master trip; Main protection operated | June | High | Permanent
2024-06-17 | 09:45 | 083/24 | Maun | Maun T2 LV CB 2T0 | 11 | Distribution | North | Clear | 11:05 | 1.33 | SCADA/Sekgatlhola | Tripped | June | High | Permanent
2024-06-28 | 15:03 | 084/24 | Ghanzi | Ghanzi T1 HV CB 110 | 11 | Distribution | North | Clear | 15:25 | 1.45 | SCADA/Rasefako | Main Trip Circuit Fail; Load loss (17.9 MW) | June | High | Permanent
2024-06-28 | 15:03 | 084/24 | Ghanzi | Ghanzi T1 LV CB 1H0 | 11 | Distribution | North | Clear | 15:25 | 1.45 | SCADA/Rasefako | HV trip received | June | High | Permanent
2024-06-28 | 15:03 | 084/24 | Ghanzi | Ghanzi Bus Section CB 1S0 | 11 | Distribution | North | Clear | 15:25 | 1.45 | SCADA/Rasefako | Buszone protection ABC | June | High | Permanent
2024-07-04 | 17:59 | 085/24 | FWST | FWST T2A LV CB 2H0A | 11 | Distribution | North | Clear | 18:33 | 0.58 | SCADA/Chawilani | Overload due to T1A outage; 75% load restored | July | High | Permanent
2024-07-05 | 06:26 | 086/24 | Tlokweng | Tlokweng T1 HV CB 110 | 11 | Distribution | South | Cloudy | 09:35 | 3.15 | SCADA/Galetshetse | Master trip; winding & REF trip | July | High | Permanent
2024-07-05 | 06:26 | 086/24 | Tlokweng | Tlokweng T1 LV CB 1HO | 11 | Distribution | South | Cloudy | 03:17 | 3.15 | SCADA/Galetshetse | Tripped | July | High | Permanent
2024-07-08 | 06:23 | 089/24 | Francistown | F/Town 11kV Bus Section CB 1SO | 11 | Distribution | North | Clear | 07:49 | 1.43 | SCADA | Tripped; Load loss (7.55 MW) | July | High | Permanent
2024-07-19 | 07:51 | 093/24 | Gab East | Gab East T1A HV CB 110A | 11 | Distribution | South | Clear | 08:37 | 0.77 | SCADA/R. Galetshetse | LV REF trip; Load loss (10 MW) | July | High | Permanent
2024-07-19 | 07:51 | 093/24 | Gab East | Gab East T1A LV CB 1H0A | 11 | Distribution | South | Clear | 08:37 | 0.77 | SCADA/R. Galetshetse | LV REF trip | July | High | Permanent
2024-07-27 | 10:02 | 096/24 | Tlokweng | Tlokweng T1 HV CB 110 | 11 | Distribution | South | Clear | 08:54 | 1.13 | SCADA/Rapelang | REF & Winding trip; Surge arrester blown | July | High | Permanent
2024-07-27 | 10:02 | 096/24 | Tlokweng | Tlokweng T1 LV CB 1HO | 11 | Distribution | South | Clear | 08:54 | 1.13 | SCADA/Rapelang | Tripped | July | High | Permanent
2024-07-27 | 10:02 | 096/24 | Tlokweng | Tlokweng T2 LV CB 2H0 | 11 | Distribution | South | Clear | 11:10 | 1.13 | SCADA/Rapelang | E/F trip; Load loss (8.5 MW) | July | High | Permanent
2024-08-29 | 02:18 | 098/24 | Tlokweng | Tlokweng T1 HV CB 110 | 11 | Distribution | South | Clear | 04:13 | 1.92 | SCADA/Galetshetse | LV Restricted Earth Fault; Through fault from CSS | August | High | Permanent
2024-08-29 | 02:18 | 098/24 | Tlokweng | Tlokweng T1 LV CB 1HO | 11 | Distribution | South | Clear | 04:13 | 1.92 | SCADA/Galetshetse | Tripped | August | High | Permanent
2024-09-04 | 05:58 | 102/24 | Tlokweng | Tlokweng T1 LV CB 1HO | 11 | Distribution | South | Clear | 17:45 | 11.78 | SCADA/Galetshetse | Tripped | September | High | Permanent
2024-09-12 | 07:51 | 103/24 | Jwaneng | Jwaneng T8 LV CB | 6.6 | Distribution | South | Clear | 08:54 | 1.05 | SCADA/Mosarwe | Tripped | September | High | Permanent
2024-09-15 | 08:01 | 105/24 | Zone 5 – Bosetu | T1 LV CB 1T0 | 11 | Distribution | North West | Clear | 12:57 | 4.93 | SCADA/Mosala | Tripped | September | High | Permanent
2024-09-15 | 08:01 | 105/24 | Zone 5 – Bosetu | T2 LV CB 2T0 | 11 | Distribution | North West | Clear | 12:57 | 4.93 | SCADA/Mosala | Tripped | September | High | Permanent
2024-09-20 | 00:56 | 107/24 | Orapa | Orapa 220/33kV T1 LV CB 1H0 | 33 | Distribution | Central | Clear | 11:19 | 50.38 | SCADA/Likokoto | Duplicate of 104/24 | September | High | Permanent
2024-09-28 | 17:41 | 109/24 | WoodHall | WoodHall T1A & T2A LV CBs | 11 | Distribution | South | Cloudy | 20:28 | 2.78 | SCADA/Kaloso | HV O/C trip; Load loss (2.1 MW) | September | High | Permanent
2024-10-11 | 16:21 | 112/24 | Jwaneng | Jwaneng T8 LV CB 8H0 | 33 | Distribution | South | Clear | 17:17 | 0.93 | SCADA | Tripped | October | High | Permanent
2024-10-14 | 19:41 | 112/24 | Francistown West | F/Town West T2A LV CB 1HOA | 11 | Distribution | North | Clear | 21:15 | 1.57 | SCADA/Chabalala | Master trip; Load loss (7.8 MW) | October | High | Permanent
2024-10-16 | 04:18 | 113/24 | G/Enclave | G/Enclave T1 LV CB 1H0 | 11 | Distribution | South | Clear | 05:39 | 1.35 | SCADA/Galetshetse | Phase trip; Bus Section CB also tripped | October | High | Permanent
2024-10-16 | 04:18 | 113/24 | G/Enclave | G/Enclave T2 LV CB 2H0 | 11 | Distribution | South | Clear | 05:39 | 1.35 | SCADA/Galetshetse | Tripped | October | High | Permanent
2024-10-16 | 04:18 | 113/24 | G/Enclave | 11kV Bus Section CB 1SO | 11 | Distribution | South | Clear | 05:39 | 1.35 | SCADA/Galetshetse | Tripped (not updating on SCADA) | October | High | Permanent
2024-11-10 | 23:36 | 137/24 | Gaphatshwa | Gaphatshwa T2 LV CB H20 | 11 | Distribution | South | Clear | 1:03 | 1.45 | SCADA/Galetshetse | Tripped | November | High | Permanent
2024-11-24 | 20:16 | 154/24 | Gaphatshwa | Gaphatshwa T3 LV CB 3H0 | 11 | Distribution | South | Clear | 21:34 | 1.32 | SCADA/Madubeko | Tripped; Load loss (5 MW) | November | High | Permanent
2024-11-24 | 20:16 | 154/24 | Gaphatshwa | Gaphatshwa T4 LV CB 4H0 | 11 | Distribution | South | Clear | 21:35 | 1.32 | SCADA/Madubeko | Tripped | November | High | Permanent
2024-12-01 | 15:38 | 161/24 | S/Phikwe | S/Phikwe 220/11kV Transformer 1 LV CB A2TO | 11 | Distribution | South | Clear | 20:12 | 4.57 | SCADA / Likokotlo | — | December | High | Permanent
2024-12-01 | 15:38 | 161/24 | S/Phikwe | S/Phikwe 220/11kV Transformer 3 LV CB A1TO | 11 | Distribution | South | Clear | 20:12 | 4.57 | SCADA / Likokotlo | — | December | High | Permanent
2024-12-06 | 02:18 | 163/24 | S/Phikwe | S/Phikwe 220/11kV Transformer 3 LV CB A1TO | 11 | Distribution | Central | Clear | 07:43 | 5.42 | SCADA / Boiditswe | 11kV Inter trip send, Master trip | December | High | Permanent
2024-12-10 | 22:33 | 166/24 | Maun | Maun 132/11kV T2 HV & LV CBs 210 & 2TO | 11 | Distribution | North/West | Clear | 23:57 | 1.37 | SCADA / Rasefako | Earth fault & Master trip; Loss of supply to Maun and surrounding areas | December | High | Permanent
2024-12-14 | 15:52 | 169/24 | Woodhall | Woodhall T1A 11kV CB 1HO | 11 | Distribution | South | Rainy | 16:40 | 0.8 | SCADA / Galetshetse | HV O/C Low set trip & I/T Rec; Load loss to Lobatse (2.2 MW) | December | High | Permanent
2024-12-14 | 15:52 | 169/24 | Woodhall | Woodhall T2A 11kV CB 2HO | 11 | Distribution | South | Rainy | 17:02 | 1.17 | SCADA / Galetshetse | TX protection trip & 11kV I/T Rec | December | High | Permanent
2024-12-31 | 18:15 | 188/24 | Woodhall | Woodhall T1A: 11kV CB 1H0 | 11 | Distribution | South | Rainy | 18:59 | 0.73 | SCADA / Charles | BUS ZONE, TRIP ZONE1, CB FAIL TRIP | December | High | Permanent
2024-12-31 | 18:15 | 188/24 | Woodhall | Woodhall T4: 33kV CB H40 | 33 | Distribution | South | Rainy | 19:11 | 0.92 | SCADA | — | December | High | Permanent
2025-01-26 | 05:37 | 020.1/25 | Woodhall | Woodhall T1A LV CB 1H0 | 11 | Distribution | South | Clear | 07:46 | 2.15 | SCADA / Galetshetse | HV O/C Low set & Standby E/F High set; CSS reported fallen 11kV conductors; Load loss 1.8 MW | January | High | Permanent
2025-02-10 | 09:22 | 067/25 | Tlokweng | Tlokweng 132/11kV T2 LV CB 2H0 | 11 | Distribution | Tlokweng | Cloudy | 18:33 | 9.18 | SCADA / Galetshetse | — | February | High | Permanent
2025-02-19 | 12:26 | 061/25 | Gaphwatshwa | Gaphwatshwa 132/33kV T2 LV CB H20 | 33 | Distribution | South | Rain | 13:03 | 0.45 | SCADA / Kaloso | LV O/C & E/F trip; Master trip | February | Medium | Sustained
2025-02-19 | 12:40 | 062/25 | Broadhurst | Broadhurst 132/33kV LV CB 4T0 | 33 | Distribution | South | Rain | 13:03 | 0.45 | SCADA / Kaloso | LV O/C & E/F trip; Master trip | February | Medium | Sustained
2025-02-28 | 11:20 | 072/25 | Mogoditshane | Mogoditshane 132/11kV T4 LV CB 4HO | 11 | Distribution | South | Clear | 12:30 | 1.17 | SCADA / A. Mangole | — | February | High | Permanent
2025-03-02 | 7:58 | 075/25 | Kanye | Kanye 132/11kV Tx 2 LV CB 2HO | 11 | Distribution | South | Rainy | 2:11 | 18.22 | SCADA / Baikgantshi | 3Ph T + L/O | March | High | Permanent
2025-03-09 | 18:30 | 077/25 | Government Enclave, 132/11kV T1 | Government Enclave 132/11kV T1 LV CB 1HO | 11 | Distribution | South | Clear | 19:55 | 1.42 | SCADA | Tripped | March | High | Permanent
2025-03-13 | 4:46 | 084/25 | F/Town West | F/Town West 132/11kV Tx 2A LV CB 2HOB | 11 | Distribution | North | Cloudy | 5:43 | 0.95 | SCADA / Chabalala | LV OC & EF Relay: Trip. LV master trip operated | March | High | Permanent
2025-03-13 | 6:23 | 084/25 | F/Town West | F/Town West 132/11kV Tx 2A LV CB 2HOB | 11 | Distribution | North | Cloudy | 7:04 | 0.68 | SCADA / Chabalala | LV OC & EF Relay: Trip. LV master trip operated | March | High | Permanent
2025-03-13 | 13:01 | 078/25 | Francistown | Francistown 220/11kV TX 1B LV CB 1TOB | 11 | Distribution | North | Cloudy | 14:12 | 1.18 | SCADA / Magola | F/town, 220/11kV TX 1B LV side; Ground to neutral, O/C trip | March | High | Permanent
2025-03-13 | 13:01 | 078/25 | Francistown | Francistown 220/11kV TX 1A LV CB 1TOA | 11 | Distribution | North | Cloudy | 17:13 | 4.2 | SCADA / Magola | F/town, 220/11kV TX 1A LV side; Backup protection trip | March | High | Permanent
2025-03-22 | 15:05 | 88/25 | Orapa 2 | Orapa 2 220/33kV T1 LV CB H08 | 33 | Distribution | Central | Clear | 16:18 | 1.22 | SCADA | LoStage E/F operated; Letlhakane Village feeder OHL conductor broken | March | High | Permanent
2025-03-28 | 19:59 | 091/25 | Gaphatshwa | Gaphatshwa 132/11kV Transformer 4 LV CB 4HO | 11 | Distribution | South | Normal | 21:55 | 1.93 | SCADA | Over voltage, Master trip operated | March | High | Permanent
2025-03-28 | 19:59 | 091/25 | Gaphatshwa | Gaphatshwa 132/11kV Transformer 3 LV CB 3HO | 11 | Distribution | South | Normal | 21:55 | 1.93 | SCADA | Over voltage, Master trip operated | March | High | Permanent
2025-04-09 | 6:46 | 095/25 | Jwaneng | Jwaneng 132/33kV Transformer 9 LV CB 9HO | 33 | Distribution | South | Rainy | 16:03 | 9.28 | SCADA / Mosarwe | Through fault from CSS Feeder 4L5 (failed to trip); restored after isolation | April | High | Permanent
2025-04-12 | 10:53 | 097/25 | Jwaneng | Jwaneng 132/33kV Transformer 9 LV CB 9HO | 33 | Distribution | South | Cloudy | 11:31 | 0.63 | SCADA / Mosarwe | Buszone trip; Mine Feeder 5 tripped on O/C, E/F | April | High | Permanent
2025-04-12 | 14:24 | 098/25 | Jwaneng | Jwaneng 132/33kV Transformer 9 LV CB 9HO | 33 | Distribution | South | Cloudy | 14:51 | 0.45 | SCADA / Mosarwe | Buszone trip; Mine Feeder 5 tripped on O/C, E/F | April | Medium | Sustained
2025-04-19 | 9:27 | 099/25 | Broadhurst | Broadhurst 132/11kV TRF 1 LV CB 3H0 | 11 | Distribution | South | Cloudy | 14:05 | 4.63 | SCADA / R. Galetshetse | Overcurrent trip; Zone 2 trip, underfrequency relay | April | High | Permanent
2025-04-19 | 9:27 | 099/25 | Broadhurst | Broadhurst 132/11kV TRF 2 LV CB 4HO | 11 | Distribution | South | Cloudy | 11:51 | 50.4 | SCADA / R. Galetshetse | Underfrequency relay trip | April | High | Permanent
2025-04-23 | 22:13 | 102/25 | Mochudi | Mochudi 132/33kV Transformer 1 LV CB 110 | 33 | Distribution | South | Clear | 0:29 | 2.27 | SCADA / E. Ntoko | Earth fault | April | High | Permanent
2025-04-30 | 7:15 | 103/25 | Jwaneng | Jwaneng 132/33kV Tx 9 LV CB 9HO | 33 | Distribution | South | Sunny | 8:03 | 0.8 | SCADA / Mosarwe | E/F trip | April | High | Permanent
2025-04-30 | 9:12 | 104/25 | Jwaneng | Jwaneng 132/33kV Tx 8 LV CB 8HO | 33 | Distribution | South | Sunny | 9:34 | 0.37 | SCADA / Mosarwe / Charles | Buszone trip; baboons seen in substation, flash on 33kV busbar | April | Medium | Sustained
2025-05-03 | 10:20 | 108/25 | Maun | Maun 132/11kV Transformer 1 LV CB 1T0 | 11 | Distribution | North | Sunny | 16:13 | 5.88 | SCADA / Magola | Protection Trip, Current Relay operated | May | High | Permanent
2025-05-03 | 10:20 | 108/25 | Maun | Maun 11kV Bus Section CB 1S0 | 11 | Distribution | North | Sunny | 16:19 | 5.98 | SCADA / Magola | Protection Trip | May | High | Permanent
2025-05-23 | 22:13 | 102/25 | Mochudi | Mochudi 132/33kV Transformer 1 LV CB 110 | 33 | Distribution | South | Clear | 0:29 | 2.27 | SCADA / E. Ntoko | Earth fault | May | High | Permanent
2025-06-08 | 11:52 | 123/25 | Phakalane | Phakalane 132/11kV Transformer 2 LV CB 2HOB | 11 | Distribution | South | Clear | 12:31 | 0.65 | SCADA | Inter trip receive | June | High | Permanent
2025-06-08 | 11:52 | 123/25 | Phakalane | Phakalane 11kV Bussection CB 1SOB | 11 | Distribution | South | Clear | 12:31 | 0.65 | SCADA | CB FAIL Right hand side | June | High | Permanent
2025-06-25 | 17:31 | 128/25 | Molepolole | Molepolole 132/33kV T1 LV CB H10 | 33 | Distribution | South | Clear | 20:48 | 3.28 | Kgame/Galetshetse | LV Directional E/F Trip | June | High | Permanent
30/01/2023 | 07:23 | 017/23 | S/Phikwe | S/Phikwe 66 Bus Section CB 120 | 66 | Sub-Transmission | South | Raining | 09:09 | 1.767 | SCADA/Miti | Bus Zone A+B trip | January | High | Permanent
22/03/2023 | 13:52 | 089/23 | Hydromet | Hydromet - Phoenix 66 Line 1 CB 505 | 66 | Sub-Transmission | North | Clear | 14:36 | 0.73 | SCADA/Garebatho | E/F protection (Red phase), A=2378A, G=2174A | March | High | Permanent
15/05/2023 | 8:43 | 133/23 | Hydromet | Hydromet - Phoenix 1 66kV line CB 505 | 66 | Sub-Transmission | North | Clear | 8:52 | 0.15 | SCADA | BCU Relay - White & Blue phase to ground; 3 ph T + L/O | May | Medium | Sustained
2023-08-06 | 11:59 | 144/23 | Lotsane | Lotsane 66kV Bus Section CB Q20 | 66 | Sub-Transmission | Central | Clear | 12:56 | 0.95 | SCADA/Gape Nthobatsang | O/C and E/F, zone 2 trip | June | High | Permanent
2023-08-06 | 11:19 | 144/23 | Morupule A | Morupule A 66kV line 2 CB 210 | 66 | Sub-Transmission | Central | Clear | 14:35 | 3.27 | SCADA/Moalosi | 3ph T + L/O | June | High | Permanent
20/06/2023 | 17:30 | 151/23 | Hydromet | Hydromet - Phoenix 1 66kV line CB 505 | 66 | Sub-Transmission | North | Clear | 17:39 | 0.15 | SCADA | 3ph T + L/O | June | Medium | Sustained
20/08/2023 | 20:58 | 151/23 | Phoenix | Phoenix - Hydromet 66kV line 2 CB 205 | 66 | Sub-Transmission | North | Clear | 21:10 | 0.2 | SCADA | 3ph T + L/O | August | Medium | Sustained
22/09/2023 | 19:49 | 161/23 | Phoenix | Phoenix 220/66kV TRF 1 HV CB H10 | 66 | Sub-Transmission | North | Clear | 07:15 | 11.43 | SCADA/Chabalala | Tertiary E/F trip, Master trip | September | High | Permanent
22/09/2023 | 19:49 | 161/23 | Phoenix | Phoenix 220/66kV TRF 1 LV CB 180 | 66 | Sub-Transmission | North | Clear | 07:15 | 11.43 | SCADA/Chabalala | Tertiary E/F trip, Master trip | September | High | Permanent
13/10/2023 | 10:29 | 172/23 | Phoenix | Phoenix 220/66kV Tx 1 HV CB H10 | 66 | Sub-Transmission | North | Clear | 11:49 | 1.33 | SCADA/Mosala | Oil temperature trip, winding temperature trip, master trip | October | High | Permanent
13/10/2023 |  | 172/23 | Phoenix | Phoenix 220/66kV Tx 1 LV CB 180 | 66 | Sub-Transmission | North | Clear | 11:49 | 1.33 | SCADA/Mosala | Tripped | October | High | Permanent
15/11/2023 | 07:14 | 199/23 | Hydromet | Hydromet - Phoenix 66kV line CB 505 | 66 | Sub-Transmission | North | Clear | 07:18 | 0.07 | SCADA | BACK UP OVERCURRENT TRIP; 3 Ph T+L/O | November | Low | Transient
26/11/2023 | 07:14 | 199/23 | Hydromet | Hydromet - Phoenix 66kV line CB 505 | 66 | Sub-Transmission | North | Clear | 07:18 | 0.07 | SCADA | BACK UP OVERCURRENT TRIP; 3 Ph T+L/O | November | Low | Transient
18/12/2023 | 13:26 | 216/23 | Lotsane | 66 kV Bus Section CB Q20 | 66 | Sub-Transmission | Central | Rain | ARC | 0 | SCADA | 3 phT+ ARC | December | Low | Transient
28/01/2024 | 15:08 | 032/24 | Jwaneng | Jwaneng 132/66kV T5 HV CB 810 | 66 | Sub-Transmission | South | Clear | 16:11 | 1.05 | SCADA / Mosarwe | Buch trip and Mastertrip; Tripped | January | High | Permanent
2024-03-16 | 21:08 | 058.3/24 | Isang Ext | Isang Ext 220/66kV TRF1 & 2 HV & LV CBs H10 & H20 | 66 | Sub-Transmission | South | Clear | 23:44 | 2.6 | SCADA | HV Timed Earth Fault | March | High | Permanent
2024-03-16 | 21:08 | 058.3/24 | Isang Ext | Isang Ext 220/66kV TRF1 & 2 HV & LV CBs H10 & H20 | 66 | Sub-Transmission | South | Clear | 23:44 | 2.6 | SCADA | HV Timed Earth Fault | March | High | Permanent
2024-06-03 | 12:25 | 081/24 | Hydromet – Phoenix 1 | Hydromet - Phoenix 1 66kV line CB 505 | 66 | Sub-Transmission | North | Clear | 13:51 | 1.43 | SCADA/Chawilani | Blue phase to ground; Load loss (0.68 MW) | June | High | Permanent
2024-06-17 | 09:41 | 083/24 | Maun | Maun T1 HV CB 110 | 111 | Sub-Transmission | North | Clear | 11:08 | 1.45 | SCADA/Sekgatlhola | Buchholz gas alarm; Load loss (17.9 MW) | June | High | Permanent
2024-10-04 | 16:54 | 111/24 | Hydromet – Phoenix 1 | Hydromet - Phoenix 1 66kV line CB 505 | 66 | Sub-Transmission | North | Clear | 18:32 | 1.63 | SCADA | BZ B/U trip; Load loss (0.5 MW) | October | High | Permanent
2024-10-04 | 16:54 | 111/24 | Hydromet – Phoenix 1 | 66kV Bus Coupler CB 130 | 66 | Sub-Transmission | North | Clear | 18:32 | 1.63 | SCADA | Diff & Instantaneous current trip | October | High | Permanent
2024-11-13 | 06:30 | 140/24 | Phikwe | 66kV Bus Bar A | 66 | Sub-Transmission | South | Clear | 11:38 | 5.13 | SCADA/Likokoto | Bus zone trip; Load loss (4 MW) | November | High | Permanent
2024-12-01 | 15:38 | 161/24 | S/Phikwe | S/Phikwe 220/66kV Transformer 5 LV CB 210 | 66 | Sub-Transmission | South | Clear | 20:12 | 4.57 | SCADA / Likokotlo | Did not trip | December | High | Permanent
2024-12-01 | 15:38 | 161/24 | S/Phikwe | S/Phikwe 220/66kV Transformer 6 LV CB 110 | 66 | Sub-Transmission | South | Clear | 20:10 | 4.53 | SCADA / Likokotlo | Did not trip | December | High | Permanent
2024-12-06 | 02:18 | 163/24 | S/Phikwe | S/Phikwe 220/66kV Transformer 6 LV CB 110 | 66 | Sub-Transmission | Central | Clear | 07:18 | 5 | SCADA / Boiditswe | — | December | High | Permanent
2025-01-21 | 15:18 | 017/25 | Hydromet – Phoenix 1 | Hydromet - Phoenix 1 66kV line CB 505 | 66 | Sub-Transmission | North | Clear | 5:49 | 14.52 | SCADA / K. Magola | 87 Trip, 79 lockout, SOTM; CSS reported mine truck hit pole at Mupane mine; Load loss 0.68 MW | January | High | Permanent
2023-02-01 | 03:28 | 002/23 | Thamaga | Thamaga - Rakola 220 line CB L45 | 220 | Transmission | South | Clear | ARC | 0 | SCADA | Distance protection trip, line DIFF protection trip Wɸ operated | January | Low | Transient
2023-05-01 | 19:30 | 003/23 | Fancistown | Francistown - Dukwe 132 Line CB 205 | 132 | Transmission | North | Storm | 20:27 | 0.95 | SCADA/Garebatho | Load loss to Sowa Mine | January | High | Permanent
2023-06-01 | 15:26 | 005/23 | Orapa | Orapa1 220/33 Transformer 1: HV CB H10 | 220 | Transmission | North | Rainy | 19:12 | 1.067 | SCADA | Diff, HV Stdby E/F & HV (IDMT) O/C protn | January | High | Permanent
2023-06-01 | 19:37 | 006/23 | Legotlhwane | Legotlhwane - Makoba 132 line CB 305 | 132 | Transmission | North/South | Rainy | ARC | 0 | SCADA | 3-phase trip + ARC indication | January | Low | Transient
2023-07-01 | 17:40 | 008/23 | Samochima | Samochima - Makoba 132 line CB 305 | 132 | Transmission | North/South | Clear | 00:16 | 6.6 | SCADA/Mosala | Tripped due to unavailability of 110V DC supply | January | High | Permanent
2023-09-01 | 16:04 | 009/23 | Phokoje | Phokoje - Insukamini 400 Line CB 2L5 | 400 | Transmission | Central | Clear | 16:25 | 0.35 | SCADA/Sekgatlhola | Master trip, DTTS, DTTR, PS L1 | January | Medium | Sustained
14/01/2023 | 02:14 | 010/21 | Morupule A | Morupule A Unit 4 220 CB G40 tripped | 220 | Transmission | Central | Clear | 09:48 | 7.567 | SCADA/Keditlwaetse | Loss of Flame, Generation dropped from 18MW to 0MW | January | High | Permanent
15/01/2023 | 12:42 | 011/23 | Phokoje | Phokoje - Insukamini 400 Line CB 2L5 | 400 | Transmission | Central | Clear | 12:46 | 0.067 | SCADA | Main A & B Master trip, DTTS, DTTR | January | Low | Transient
17/01/2023 | 17:52 | 112/23 | Phokoje | Phokoje - Insukamini 400 Line CB 2L5 | 400 | Transmission | Central | Clear | 18:34 | 0.7 | SCADA/Miti | Main A: Master trip, DTTS, DTTR | January | High | Permanent
26/01/2023 | 08:31 | 015/23 | Morupule A | Morupule A Unit 4 220 CB G40 tripped | 220 | Transmission | Central | Clear | 13:21 | 4.833 | SCADA/DICK | Generator reverse power trip | January | High | Permanent
26/01/2023 | 10:34 | 116/23 | Phokoje | Phokoje - 400/220 TRF 2: HV CB 2H0 | 400 | Transmission | Central | Clear | 14:45 | 4.183 | SCADA/Miti | Buchholz trip due to valve issue during maintenance | January | High | Permanent
29/01/2023 | 22:34 | 016/23 | Orapa | Orapa 1 220/33 Transformer 1: HV CB H10 | 220 | Transmission | Central | Rainy | 00:31 | 1.95 | SCADA | MASTER TRIP | January | High | Permanent
31/01/2023 | 09:18 | 019/23 | Phokoje | Phokoje - Insukamini 400 Line CB 2L5 | 400 | Transmission | Central | Clear | 13:29 | 4.183 | SCADA/Miti | Power Swing, Master trip, DTTS, DTTR | January | High | Permanent
31/01/2023 | 13:38 | 020/23 | Fancistown | Francistown - Dukwe 132 Line CB 205 | 132 | Transmission | North | Storm | 13:42 | 0.067 | SCADA/Garebatho | Load loss to Sowa Mine | January | Low | Transient
31/01/2023 | 17:56 | 021/23 | Makoba | Makoba- Samochima 132 line CB 105 | 132 | Transmission | North West | Clear | 19:20 | 1.4 | SCADA | General trip, Impedance Zone 1, Bus CB Fail | January | High | Permanent
2023-05-02 | 00:53 | 028/23 | Motheo Mine | Motheo Mine 132/11 T1: HV CB 110 | 132 | Transmission | North West | Clear | 18:41 | 17.8 | SCADA/Miti | Master Trip(A), TCSR(M), TCSR(Bu), TOP, CAR 3 & CAR 4 | February | High | Permanent
2023-05-02 | 13:00 | 028/23 | Phokoje | Phokoje - 400/220 TRF 2: HV CB 2H0 | 400 | Transmission | Central | Clear | 18:41 | 5.683 | SCADA/Miti | Master Trip(A), TCSR(M), TCSR(Bu), TOP, CAR 3 & CAR 4 | February | High | Permanent
2023-07-02 | 10:23 | 030/23 | Morupule A | Morupule A Unit 3 tripped | 220 | Transmission | Central | Clear | 16:32 | 6.15 | SCADA/Gabatshamekwe | Unit trip, restoration after investigation | February | High | Permanent
2023-07-02 | 14:34 | 031/23 | Thamaga | Thamaga - Jwaneng 2 132 Line CB 505 | 132 | Transmission | South | Thunder Storm | ARC | 0 | SCADA | Zone 1 Impedance trip, 1-phase trip + ARC, fault at 64.2km | February | Low | Transient
2023-08-02 | 18:03 | 034/23 | Phokoje | Phokoje - Insukamini 400 Line CB 2L5 | 400 | Transmission | Central | Clear | 18:14 | 0.183 | SCADA/Sekgatlhola | Main A & B Master trip, DTTS, DTTR, PS L1 | February | Medium | Sustained
2023-09-02 | 00:00 | 037/23 | Morupule | MORPB - MORPA 400/220 Intertie Tx HV CB 1TO | 400 | Transmission | Central | Rain | ARC | 0 | SCADA/Moalosi | F1 & F2 Current Diff Prot, Multi-Terminal Relay trip, UV, lockout | February | Low | Transient
13/02/2023 | 20:35 | 040/23 | Mawana | Mmakgodumo - Kanye 132 line CB 305 | 132 | Transmission | South | Rainy | 22:28 | 1.883 | SCADA/Baoki | I/T send, Current diff and OC/EF | February | High | Permanent
14/02/2023 | 15:35 | 041/23 | Ghanzi | Ghanzi 132/11 Transformer 1 HV CB 110B | 132 | Transmission | North | Rainy | 16:45 | 1.167 | SCADA/Kahona | No indications, control issue suspected | February | High | Permanent
16/02/2023 | 00:20 | 045/23 | Rakola | Rakola - Molepolole 132 Line CB 205 | 132 | Transmission | South | Rainy | 02:52 | 2.533 | SCADA | SOTF, W & B Phase Imp E/F | February | High | Permanent
16/02/2023 | 05:06 | 048/23 | Segoditshane | Segoditshane - Rakola 132 line CB L25 | 132 | Transmission | South | Rainy | 05:55 | 0.817 | SCADA | DTTR I/T S/R trip, 3-phase trip+L/O | February | High | Permanent
16/02/2023 | 15:01 | 049/23 | Fancistown | F/town - Dukwe 132 line CB 205 | 132 | Transmission | South | Rainy | 15:03 | 0.033 | SCADA | Zm1-Zm3, PST, PSW, PSN, CRZ, CSZ; Distance to fault: 81.4km | February | Low | Transient
18/02/2023 | 20:24 | 050/23 | Fancistown | Dukwe - F/town 132 line CB 505 | 132 | Transmission | North | Storm | 20:34 | 0.167 | SCADA/Sere | 48V DC mains fail, short outage, auto-reclose | February | Medium | Sustained
18/02/2023 | 22:45 | 055/23 | Segoditshane | Segs - Dwaarsberg 132 Line CB 905 | 132 | Transmission | South | Cloudy | 22:45 | 0 | SCADA | 1-phase trip + ARC, no restoration | February | Low | Transient
19/02/2023 | 00:09 | 056/23 | Segoditshane | Segs - Dwaarsberg 132 Line CB 905 | 132 | Transmission | South | Cloudy | 00:56 | 0.783 | SCADA | 3-phase trip + L/O | February | High | Permanent
20/02/2023 | 14:37 | 059/23 | Phokoje | Phokoje - Insukamini 400 Line CB 2L5 | 400 | Transmission | North | Rainy | 14:45 | 0.133 | SCADA | Under Frequency, Main A: Master trip, DTTS, DTTR, PSL1-3 | February | Medium | Sustained
20/02/2023 | 15:30 | 060/23 | Phokoje | Phokoje - Insukamini 400 Line CB 2L5 | 400 | Transmission | North | Rainy | ARC | 0 | SCADA | Master trip, no restoration indication likely ARC | February | Low | Transient
21/02/2023 | 21:52 | 061/23 | Thamaga | Thamaga - Rakola 220 line CB L45 | 220 | Transmission | South | Clear | 21:54 | 0.033 | SCADA | DIFF trip, 3-phase trip+L/O | February | Low | Transient
24/02/2023 | 18:05 | 063/23 | Phokoje | Phokoje - Insukamini 400 line CB 2L5 | 400 | Transmission | Central | Clear | 18:10 | 0.083 | SCADA | Main B power swing, DIR Trans Receive, Master Trip, Protection Trip | February | Low | Transient
2023-03-03 | 18:03 | 079/23 | Phokoje | Phokoje - Insukamini 400 Line CB 2L5 | 400 | Transmission | Central | Clear | 18:14 | 0.183 | SCADA/Sekgatlhola | Main A & B Master trip, DTTS, DTTR, PS L1 | March | Medium | Sustained
2023-07-03 | 15:47 | 082/23 | Phokoje | Phokoje - Insukamini 400 Line CB 2L5 | 400 | Transmission | Central | Rainy | 16:23 | 0.6 | SCADA | Master trip, DTTS, DTTR, PS L1, Distance to fault: 56.2km | March | High | Permanent
2023-09-03 | 16:15 | 083/23 | Phokoje | Phokoje - Insukamini 400 Line CB 2L5 | 400 | Transmission | Central | Clear | 16:25 | 0.167 | SCADA | Main A: Master trip, DTTS, DTTR, PS L1 | March | Medium | Sustained
2023-10-03 | 14:45 | 084/23 | Phokoje | Phokoje - Insukamini 400 Line CB 2L5 | 400 | Transmission | Central | Clear | 14:52 | 0.117 | SCADA | Main B: Master trip, DTTS, DTTR, PS L1 | March | Medium | Sustained
14/03/2023 | 16:09 | 076/23 | Thamaga | Thamaga - Rakola 220 line CB L45 | 220 | Transmission | South | Clear | 16:20 | 0.183 | SCADA | DIFF trip, 3-phase trip + L/O | March | Medium | Sustained
15/03/2023 | 16:16 | 082/23 | Ramotswa | Ramotswa - Woodhall 132 Line CB 105 | 132 | Transmission | South | Cloudy | 17:32 | 1.27 | SCADA/Ramacha | BU protection Relay: lockout trip, TCS unhealthy, 87L trip, fault at 3.8km | March | High | Permanent
15/03/2023 | 16:35 | 082/23 | Thamaga | Thamaga - Jwaneng 132 line 1 CB 305 | 132 | Transmission | South | Cloudy | ARC | 0 | SCADA/Bonno | 1-phase trip + ARC | March | Low | Transient
19/03/2023 | 14:34 | 105/23 | Morupule A | MORP A - Serule 220 Line CB L15 | 220 | Transmission | Central | Rainy | 15:20 | 0.77 | SCADA | Distance Zone 1 & 2, 3-phase trip + L/O | March | High | Permanent
21/03/2023 | 13:52 | 085/23 | Orapa | Letlhakane - Karowe 132 Line CB 305 | 132 | Transmission | North | Rainy | 14:36 | 0.7 | SCADA/Orapa | 3-phase trip, distance to fault 48.2km, load loss reported | March | High | Permanent
31/03/2023 | 08:29 | 097/23 | Gabane South | Gabane South - Dwaarsberg 132 Line CB 105 | 132 | Transmission | South | Clear | 08:40 | 0.183 | SCADA/Kololo | Imp trip Z1, Z2, DTTS, 3-phase trip + L/O | March | Medium | Sustained
31/03/2023 | 15:40 | 106/23 | Makoba | Makoba - Samochima 132 Line CB 105 | 132 | Transmission | North West | Storm | 16:42 | 1.03 | SCADA | General trip, Impedance Zone 1, Bus CB Fail, ARC initiated | March | High | Permanent
31/03/2023 | 17:38 | 107/23 | Mmakgodumo | Mmakgodumo - Thamaga 132 Line CB 205 | 132 | Transmission | South | Cloudy | 18:22 | 0.73 | SCADA | Zone 1 Impedance, 3-phase trip + L/O, fault at 88.6km | March | High | Permanent
22/04/2022 | 9:17 | 120/23 | Letlhakane | Letlhakane 220/132kV TRF 4 LV CB 480 | 132 | Transmission | North/West | Clear | 9:45 | 0.47 | SCADA | Letlhakane 220/132kV TRF 4 and Karowe 132kV income line CB 105 tripped while Contractor was injecting a signal after simulating a Blue phase fault trip. | April | Medium | Sustained
22/04/2022 | 9:17 | 120/23 | Letlhakane | HV CB H40 | 132 | Transmission | North/West | Clear | 9:45 | 0.47 | SCADA | Letlhakane 220/132kV TRF 4 and Karowe 132kV income line CB 105 tripped while Contractor was injecting a signal after simulating a Blue phase fault trip. | April | Medium | Sustained
22/04/2022 | 9:17 | 120/23 | Karowe | Karowe -Letlhakane132kV line CB 105 | 132 | Transmission | North/West | Clear | 9:45 | 0.47 | SCADA | Letlhakane 220/132kV TRF 4 and Karowe 132kV income line CB 105 tripped while Contractor was injecting a signal after simulating a Blue phase fault trip. | April | Medium | Sustained
2023-06-04 | 1:27 | 104/23 | Segs | Segs - Dwaarsberg 132kV line CB 905 | 132 | Transmission | South | Cloudy | 1:39 | 0.2 | SCADA | No load loss | April | Medium | Sustained
2023-07-04 | 8:07 | 105/23 | SEGS | SEGS - BDHT/MOGS 1 132kV line CB 605 | 132 | Transmission | South | Clear | 8:59 | 0.87 | SCADA | Ramotswa & Gabane / Mochudi 33kV line feeders. | April | High | Permanent
2023-07-04 | 8:07 | 105/23 | Gabane | Gab south - Tlokweng 132kV line CB 905 | 132 | Transmission | South | Clear | 11:31 | 3.4 | SCADA / Charles |  | April | High | Permanent
2023-08-04 | 5:32 | 107/23 | Morupule A | MORP A - Serule line CB L65 | 220 | Transmission | Central/South | CLEAR | 2:14 | 1.65 | SCADA/.Moalosi | No load loss | April | High | Permanent
2023-08-04 | 5:32 | 107/23 | Serule | Serule - MORP A line CB L55 | 220 | Transmission | Central/South | CLEAR | 2:14 | 1.65 | SCADA/Sekgatlhola | No load loss | April | High | Permanent
2023-09-04 | 2:55 | 108/23 | Kgale | Kgale view 132kv line CB 405 | 132 | Transmission | South | Cloudy | 3:25 | 0.5 | SCADA/KOLOLO | It was advised that the line did not trip at Jwaneng End. | April | Medium | Sustained
2023-09-04 | 2:55 | 108/23 | Kgale | 132 Kv Bus Coupler CB 230 | 132 | Transmission | South | Cloudy | 3:25 | 0.5 | SCADA/KOLOLO |  | April | Medium | Sustained
2023-09-04 | 2:55 | 108/23 | Thamaga | 220/132 Kv T2 : HV CB H20 | 132 | Transmission | South | Clear | 3:25 | 0.5 | SCADA/KOLOLO | It was advised that the line did not trip at Jwaneng End. | April | Medium | Sustained
2023-09-04 | 2:55 | 108/23 | Thamaga | :LV CB 280 | 132 | Transmission | South | Clear | 3:25 | 0.5 | SCADA/KOLOLO |  | April | Medium | Sustained
2023-11-04 | 4:21 | 110/23 | Thamaga | Mmakgodumo - Thamaga 132kV Line CB 105 | 132 | Transmission | South | Clear | 7:04 | 2.72 | SCADA /BAOKI | No load loss | April | High | Permanent
2023-11-04 | 4:21 | 110/23 | Thamaga | Thamaga - Mmakgodumo 132kV Line CB 205 | 132 | Transmission | South | Clear | 7:03 | 2.7 | SCADA/KOLOLO | No load loss | April | High | Permanent
2023-11-04 | 4:21 | 110/23 | Thamaga | 220/132 Transformer HV CB H10 | 132 | Transmission | South | Clear | 7:05 | 2.73 | SCADA/MAKOKO | No load loss | April | High | Permanent
2023-11-04 | 4:21 | 110/23 | Thamaga | 220/132 Transformer LV CB 180 | 132 | Transmission | South | Clear | 7:05 | 2.73 | SCADA/MAKOKO | No load loss | April | High | Permanent
2023-11-04 | 4:21 | 110/23 | Thamaga | 132kV Bus Coupler CB 230 | 132 | Transmission | South | Clear | 7:03 | 2.7 | SCADA/MAKOKO | No load loss | April | High | Permanent
2023-12-04 | 17:49 | 112/23 | Segs | Segoditshane- Phakalane 132kV line CB 805 | 132 | Transmission | South | Clear | 19:59 | 2.18 | SCADA | PHAKALANE SUB, load loss | April | High | Permanent
2023-12-04 | 17:49 | 112/23 | Phakalane | Phakalane- segoditshane 132kV line CB 105 | 132 | Transmission | South | Clear | 20:12 | 2.42 | NIL | Did not trip. Switched off as precaution. | April | High | Permanent
13/04/2023 | 21:37 | 114/23 | MORP | MORP A - Serule line CB L65 | 220 | Transmission | Central/South | CLEAR | 23:19 | 1.7 | SCADA/.Moalosi | No load loss | April | High | Permanent
13/04/2023 | 21:37 | 114/23 | Serule | Serule - MORP A line CB L55 | 220 | Transmission | Central/South | CLEAR | 23:20 | 1.72 | SCADA/Sekgatlhola | No load loss | April | High | Permanent
17/04/2023 | 14:31 | 116/23 | Letlhakane | Letlhakane 220/132kV TRF4 LV CB 480 | 132 | Transmission | North / West | CLEAR | 15:43 | 1.2 | SCADA/Theophillus | This trip occurred when works under LOA 321/23 was on progress, with trip links removed and B/Z relay OFF. SNR Eng. Advised that LOA should be cancelled and prepare for another one for investigating this wrong tripping. | April | High | Permanent
17/04/2023 | 14:31 | 116/23 | Letlhakane | 132kV B/Coupler CB 530 | 132 | Transmission | North / West | CLEAR | 15:43 | 1.2 | SCADA/Theophillus | This trip occurred when works under LOA 321/23 was on progress, with trip links removed and B/Z relay OFF. SNR Eng. Advised that LOA should be cancelled and prepare for another one for investigating this wrong tripping. | April | High | Permanent
21/04/2023 | 19:04 | 120/23 | Phokoje | Phokoje - Insukamini 400kV line CB 2L5 | 400 | Transmission | North | Clear | 19:09 | 0.08 | Scada | No load loss | April | Low | Transient
21/04/2023 | 19:04 | 120/23 | Insukamini | Insukamini - Phokoje 400kV line | 400 | Transmission | North | Clear | 19:19 | 0.25 | ZESA | No load loss | April | Medium | Sustained
2023-05-05 | 15:15 | 124/23 | SEGS | SEGS - B/HURST - MOGS 2 132kV line CB 405 | 132 | Transmission | South | Clear | 16:55 | 1.67 | SCADA/SELEI | O/C & Directional E/F Relay: white, blue phase to ground; 3ph Trip + LO | May | High | Permanent
2023-05-05 | 15:15 | 124/23 | MOGS | MOGS - RAKOLA 132kV line CB 305 | 132 | Transmission | South | Clear | 19:33 | 4.3 | SCADA | Impedance start Z3, L1-L3; 3ph Trip + LO | May | High | Permanent
2023-06-05 | 4:14 | 127/23 | Segoditshane | Segoditshane - Dwarsberg 132kV line CB 905 | 132 | Transmission | South | Clear | 4:45 | 0.52 | SCADA | 3ph T + L/O | May | High | Permanent
2023-08-05 | 0:13 | 128/23 | Phokoje | Phokoje - Matimba 400kV line CB 3L5 | 400 | Transmission | IPS | Clear | 0:53 | 0.67 | Scada/Sekgatlhola | Directional E/F, Z1, Red phase trip, DTT; 3 ph T + L/O | May | High | Permanent
2023-08-05 | 0:13 | 128/23 | Matimba | Matimba - Phokoje 400kV line | 400 | Transmission | IPS | Clear | 0:20 | 0.12 | ZESA | S ph T + ARC + 3ph T + L/O & White ph to ground | May | Medium | Sustained
2023-08-05 | 0:16 | 128/23 | Mowana | Mowana - Dukwe 132kV line CB 105 | 132 | Transmission | IPS | Clear | 5:22 | 5.1 | SCADA | Overvoltage; 3 ph T + L/O | May | High | Permanent
2023-08-05 | 0:21 | 128/23 | SEGS | SEGS - DWARSBERG 132kV line CB 905 | 132 | Transmission | IPS | Clear | 4:52 | 4.52 | Ntoko | OC & EF trip & Zone 2 trip; 3 ph T + L/O | May | High | Permanent
20/05/2023 | 20:39 | 137/23 | Morupule A | Morupule A - Generator 3 | 132 | Transmission | Central | Clear | 23:30 | 2.85 | SCADA | Electronic Protection Gen trip; No interruption of supply | May | High | Permanent
23/05/2023 | 22:11 | 139/23 | Phokoje | Phokoje - Insukamini 400kV line CB 2L5 | 400 | Transmission | North | Clear | 23:10 | 0.98 | SCADA | MN A RED PH, DTTR, PERM I/T SEND, MN B MTR, MN A MTR; DTTS; 3phT+L/O | May | High | Permanent
2023-02-06 | 10:48 | 141/23 | Gov/Enclave | Gov/Enclave 132/33kV Transformer 2 HV CB 210 | 132 | Transmission | South | Clear | 11:25 | 0.62 | SCADA/MOSALA | High set O/C on CSS feeder; tripped | June | High | Permanent
2023-09-06 | 4:02 | 145/23 | Morupule A | Morupule A - Serule 220kV line CB L55 | 220 | Transmission | Central/North | Clear | 5:58 | 1.93 | Scada / Moalosi | Dist Protn Relay: DTT, 2L2 trip, Blue Phase to neutral, Zone 1 trip | June | High | Permanent
2023-09-06 | 4:02 | 145/23 | Serule | Serule - Morupule A 220kV line CB L65 | 220 | Transmission | Central/North | Clear | 6:01 | 1.98 | Scada / Sekgatlhola | Dist Protn Relay: DTT & MT | June | High | Permanent
2023-09-06 | 4:02 | 145/23 | Phokoje | Phokoje - Serule 220kV line CB L35 | 220 | Transmission | Central/North | Clear | 4:53 | 0.85 | Scada/Sekgatlhola | MN B-Dist Protn Relay: PSL2, PSN, MT, DTTS & CAR 3&4 | June | High | Permanent
2023-09-06 | 4:02 | 145/23 | Orapa | Orapa 2 - Serule 220kV line CB L15 | 220 | Transmission | Central/North | Clear | 4:16 | 0.23 | Scada | Blue phase to Ground & O/C instantaneous trip | June | Medium | Sustained
16/06/2023 | 4:12 | 148/23 | SEGS | SEGS - Spitskop 132kV line CB 905 | 132 | Transmission | South | Clear | 4:42 | 0.5 | SCADA | 3ph T + L/O | June | Medium | Sustained
19/06/2023 | 11:07 | 149/23 | Isang | Isang - Segoditshane 220kV line CB L25 | 220 | Transmission | South | Stormy | 11:09 | 0.03 | SCADA/NTOKO | DTT Send/Receive, Permissive Trip; 3-ph T + L/O; Fault: L3-Earth | June | Low | Transient
29/06/2023 | 2:28 | 154/23 | Motheo | Motheo - Motheo Mine 132 Line: CB 305 | 132 | Transmission | North West | Clear | 4:07 | 1.65 | Scada/CSS | CB trip, Master trip, TCL 1/2, TCS; Back up Protection: TRL 1/2/3, Over Current trip; 3ph trip + L/O | June | High | Permanent
29/06/2023 | 2:28 | 154/23 | Motheo Mine | Motheo Mine - Motheo 132 Line: CB 105 | 132 | Transmission | North West | Clear | 4:07 | 1.65 | Scada/CSS | 3ph trip + ARC | June | High | Permanent
03/07/2023 | 13:26 | 155/23 | Tsabong | Tsabong - Heuning Vlei 132kV line CB 105 | 132 | Transmission | North West | Clear | 20:12 | 6.77 | Mosarwe | Blue phase Trip; 3 ph T + L/O | July | High | Permanent
03/07/2023 | 13:26 | 155/23 | Heuning Vlei | Heuning Vlei 132kV line | 132 | Transmission | South | Clear | 19:02 | 5.6 | Eskom | E/F trip; 3 ph T + L/O | July | High | Permanent
11/07/2023 | 08:02 | 156/23 | Karowe | Karowe - Letlhakane 132kV line CB 105 | 132 | Transmission | North West | Clear | 12:29 | 4.45 | B. Chabalala | TCS alarm, MCB BI trip, SYNC BLK AR; 3 ph T + L/O | July | High | Permanent
29/07/2023 | 18:00 | 147/23 | Gabsouth | Gabsouth - Dwaarsberg 132kV Line CB 105 | 132 | Transmission | South | Clear | 18:19 | 0.32 | SCADA | Zone 1 Trip; Fault loop L1 to Neutral; 3ph T + LO | July | Medium | Sustained
11/09/2023 | 21:22 | 153/23 | Serule | Serule 220kV Line CB L15 | 220 | Transmission | North | Clear | 21:24 | 0.03 | SCADA/Sekgatlhola | Zone 1 Trip, Ph C To Ground; 3 ph T + L/O | September | Low | Transient
12/09/2023 | 04:08 | 154/23 | Orapa 2 | Orapa 2 220kV Line CB L15 | 220 | Transmission | North | Clear | 04:26 | 0.3 | SCADA | 3 ph T + L/O | September | Medium | Sustained
12/09/2023 | 10:16 | 155/23 | Serule | Serule - Orapa 2 220kV Line CB L15 | 220 | Transmission | North | Clear | 14:47 | 4.52 | SCADA | Zone 1 trip, Phase A to ground. Distance to fault: 91km | September | High | Permanent
12/09/2023 | 10:16 | 155/23 | Orapa 2 | Orapa - Serule 220kV Line CB L15 | 220 | Transmission | North | Clear | 14:45 | 4.48 | SCADA/Moalosi | Main 1: Red phase to ground, distance to fault: 139.14km. Main 2: Trip, instantaneous, Phase A to Ground, Zone 1 | September | High | Permanent
16/09/2023 | 16:00 | 156/23 | Serule | Serule - Orapa 2 220kV Line CB L15 | 220 | Transmission | North | Clear | 16:11 | 0.18 | SCADA | Instantaneous Trip, Red phase to ground, Zone 1. Distance to fault: 110.2km | September | Medium | Sustained
16/09/2023 | 16:00 | 156/23 | Orapa 2 | Orapa - Serule 220kV Line CB L15 | 220 | Transmission | North | Clear | 16:11 | 0.18 | SCADA | Main 1: Trip. Main 2: Trip, instantaneous, Zone 1, Phase A to Ground, Distance to fault: 115.92km | September | Medium | Sustained
17/09/2023 | 13:32 | 157/23 | Serule | Serule - Orapa 2 220kV Line CB L15 | 220 | Transmission | North | Clear | 13:51 | 0.32 | SCADA | Distance Protection Relay: Instantaneous Trip, Blue phase to ground, Zone 1, CB Pole discrepancy trip. Distance to fault: 92.32km | September | Medium | Sustained
17/09/2023 | 13:32 | 157/23 | Orapa 2 | Orapa - Serule 220kV Line CB L15 | 220 | Transmission | North | Clear | 13:51 | 0.32 | SCADA | Main 1: Trip. Main 2: Trip, instantaneous trip, Zone 2, zone 4, Phase C to Ground, SOTF, Distance to fault: 126km | September | Medium | Sustained
21/09/2023 | 10:23 | 159/23 | Morupule B | Morupule B - Letlhakane 400kV line CB 2L5 | 400 | Transmission | Central/North West | Clear | 11:03 | 0.67 | SCADA/Moloinoga | Distance Protection Relay: Gen trip, ZM trip, CAR, Blue phase to Ground; 3ph trip + L/O | September | High | Permanent
21/09/2023 | 10:23 | 159/23 | Letlhakane | Letlhakane - Morupule B 400kV line CB 3L5 | 400 | Transmission | Central/North West | Clear | 11:10 | 0.78 | SCADA/Ntoko | Main 1: Trip ZM trip, phase to Ground, lockout. Main 2: ZM trip, ARC lockout; 3ph trip + L/O | September | High | Permanent
21/09/2023 | 21:47 | 160/23 | Morupule A | Morupule A Unit 4 220kV CB G40 | 220 | Transmission | Central | Clear | 5:03 | 7.27 | SCADA/Mothobi | Flame failure; Tripped | September | High | Permanent
01/10/2023 | 19:10 | 166/23 | Dukwi | Dukwi - Sua 132kV line CB 305 | 132 | Transmission | North | Clear | 5:00 | 9.83 | SCADA | Distance Protection Relay: 3PHASE TRIP, ZONE 1 TRIP, DIST TO FAULT: 36.9 KM | October | High | Permanent
05/10/2023 | 12:37 | 168/23 | SEGS | SEGS - BDHT/MOGS 1 132kV line CB 605 | 132 | Transmission | South | Clear | 13:14 | 0.62 | SCADA | O/C Directional E/F Relay: R-PH, W-PH to Ground, Hi Set O/C trip, Master Trip | October | High | Permanent
05/10/2023 | 12:37 | 168/23 | Gabane | Gab south - Tlokweng 132kV line CB 905 | 132 | Transmission | South | Clear | 13:57 | 1.33 | SCADA / Ntoko | R-PH, W-PH, B-PH; 3ph Trip + LO | October | High | Permanent
10/10/2023 | 23:03 | 171/23 | Tlokweng | Tlokweng - Gab South 132kV line CB 905 | 132 | Transmission | South | Lightning & Thunderstorms | 0:09 | 1.1 | SCADA/Galetshetse | 3ph Trip + LO | October | High | Permanent
14/10/2023 | 13:26 | 175/23 | Mmakgodumo | Mmakgodumo - Thamaga 132kV line CB 205 | 132 | Transmission | North | Clear | 13:30 | 0.07 | SCADA/Mosarwe | Blue phase Trip; 3 ph T + L/O | October | Low | Transient
24/10/2023 | 12:21 | 177/23 | Lobatse | Lobatse - Mmakgodumo 132kV line CB 205 | 132 | Transmission | North | Clear | 13:05 | 0.73 | SCADA/Ramacha | Line Current Diff: Red, White and Blue phase Diff trip; 3ph T + L/O | October | High | Permanent
24/10/2023 | 23:12 | 178/23 | Morupule A | 220kV Bus Coupler CB W10 | 220 | Transmission | Central | Clear | 1:41 | 2.48 | SCADA/Moalosi | 86 BC; TRIP | October | High | Permanent
24/10/2023 | 23:12 | 178/23 | Phokoje | Phokoje - Morupule A 220kV line CB L55 | 220 | Transmission | Central | Clear | 1:36 | 2.4 | SCADA/Sekgatlhola | White phase-N trip, Zone 2 trip, 21L trip, 3 phase trip, Zone 2 & 3 start, 21L ext start, R & W start, L/O start, Dist: 95.3km | October | High | Permanent
28/10/2023 | 19:54 | 179/23 | Morupule B | Morupule B 400/220kV intertie TX HV CB 1TO | 220 | Transmission | Central | Clear | 21:43 | 1.82 | Scada/Moloinoga | No indications; Tripped | October | High | Permanent
28/10/2023 | 19:54 | 179/23 | Isang | Isang - Morupule A 2 220kV line CB L45 | 220 | Transmission | Central | Clear | 19:55 | 0.02 | Scada | Instantenious E/F, Master trip; 3pH trip + LO | October | Low | Transient
28/10/2023 | 19:59 | 179/23 | Morupule A | Morupule A - Isang 2 220kV line CB L25 | 220 | Transmission | Central | Clear | 20:02 | 0.05 | Scada | Distance Protn Zone 1 Red and White phases; 3 pH T+ L/O | October | Low | Transient
30/10/2023 | 13:01 | 180/23 | Isang 2 | Isang 2 - Morp A 2 220kV Line CB L45 | 220 | Transmission | South / North | Clear | 13:03 | 0.03 | SCADA / Makoko | Main 1 Relay: VT Fuse fail, Carrier aided trip, CB trip L1,L2,L3 3 phase trip, Trip signal IL2, Distance to 13.6KM, Fault REL distance 6.12%; Fault loop L2N | October | Low | Transient
30/10/2023 | 16:30 | 181/23 | Legotlhwane | Legotlhwane - Makoba 132kV Line CB 305 | 132 | Transmission | South / North | Clear | 20:34 | 4.07 | SCADA / Rasefako | Main Protection Relay: Protection trip, Imp trip z1, L2 Start, Permissive trip Receive/Send, ARC Initiate | October | High | Permanent
30/10/2023 | 16:30 | 181/23 | Makoba | 132kV Line Reactor CB 350 | 132 | Transmission | South / North | Clear | 20:34 | 4.07 | SCADA / Rasefako | Main Protection Relay: Low start E/F trip; B/UP Relay: Low start E/F Start, Master trip | October | High | Permanent
31/10/2023 | 08:09 | 182/23 | Mmakgodumo | Mmakgodumo - Lobatse 132kV Line CB 205 | 132 | Transmission | South / North | Clear | 08:11 | 0.03 | SCADA / Mosarwe | Current Differential Relay: Trip, Phase C to ground, 87; 3ph Trip + L/O | October | Low | Transient
31/10/2023 | 17:49 | 183/23 | Makoba | Makoba - Samochima 132kV line CB 105 | 132 | Transmission | North West | Clear | 17:50 | 0.02 | SCADA | Impedance Protn Zone 1, General trip; 3ph Trip + L/O | October | Low | Transient
01/11/2023 | 16:55 | 184/23 | Orapa 2 | Orapa 2 220kV line CB L15 | 220 | Transmission | North | Cloudy | 17:18 | 0.38 | Scada | Distance protn Zone 1; 3ph T + L/O | November | Medium | Sustained
05/11/2023 | 16:07 | 186/23 | Makoba | Makoba - Samochima 132kV Line CB 105 | 132 | Transmission | North West | Cloudy | 20:47 | 4.67 | SCADA / Rasefako | Protection Trip, Low set E/F trip, Pole discrepancy; 3ph Trip + L/O | November | High | Permanent
05/11/2023 |  | 186/23 | Samochima | Samochima - Makoba 132kV Line CB 305 | 132 | Transmission | North West | Cloudy | 22:44 | 6.62 | SCADA / Rasefako | Back up trip protections, Low set E/F trip, Main 1: Permissive send; 3ph Trip + L/O | November | High | Permanent
13/11/2023 | 06:00 | 190/23 | Woodhall | Woodhall T1A & T2A LV CBs 1H0 and 2H0 | 132 | Transmission | South | Clear | 06:40 | 0.67 | SCADA | HV OC low set; Tripped | November | High | Permanent
17/11/2023 | 06:04 | 191/23 | Gab East | Gab East 132/11kV T2B HV CB 210B | 132 | Transmission | South | Clear | 07:57 | 1.93 | SCADA / Ntoko | Trip, Instantaneous VT fail, Under frequency | November | High | Permanent
18/11/2023 | 00:41 | 192/23 | Gab East | Gab East 132/11kV T1B HV CB 110B | 132 | Transmission | South | Clear | 02:56 | 2.25 | SCADA / Ntoko | Phase A & B trip | November | High | Permanent
18/11/2023 |  | 192/23 | Gab East | Gab East 132/11kV T2B HV CB 210B | 132 | Transmission | South | Clear | 02:57 | 2.27 | SCADA / Ntoko | Phase A & B trip | November | High | Permanent
18/11/2023 | 16:21 | 194/23 | Gabs South | Gabs South - Ramotswa 132kV line CB 205 | 132 | Transmission | South | Cloudy | 17:27 | 1.1 | SCADA / Galetshetse | Differential; 3ph T + L/O | November | High | Permanent
18/11/2023 |  | 194/23 | Ramotswa | Ramotswa - Gabs South 132kV line CB 205 | 132 | Transmission | South | Cloudy | 18:14 | 1.88 | SCADA / Galetshetse | Differential; 3ph T + L/O | November | High | Permanent
21/11/2023 | 21:10 | 198/23 | Samochima | Samochima - Makoba 132kV line CB 305 | 132 | Transmission | North West | Cloudy / Rainy | 21:12 | 0.03 | SCADA | General trip, EF protn trip; 3 Ph T+L/O | November | Low | Transient
24/11/2023 | 12:21 | 177/23 | Lobatse | Lobatse - Mmakgodumo 132kV line CB 205 | 132 | Transmission | North | Clear | 13:05 | 0.73 | SCADA/Ramacha | Line Current Diff: Red, White and Blue phase Diff trip; 3ph T + L/O | November | High | Permanent
27/11/2023 | 23:45 | 200/23 | Rakola | Rakola- Gaphatshwa 132kV line CB 505 | 132 | Transmission | South | Cloudy / Rainy / Thunderstorms | 23:46 | 0.02 | SCADA | INSTATNTENEOUS O/C TRIP; 3 Ph T+L/O | November | Low | Transient
28/11/2023 | 17:55 | 191/23 | Gabsouth | Gabsouth - Spitskop 132kV Line CB 505 | 132 | Transmission | South | Clear | 18:34 | 0.65 | SCADA / Ntoko | B/UP: trip, protection trip; 1ph trip+L/O | November | High | Permanent
07/12/2023 | 20:18 | 202/23 | Gabsouth | Gabsouth - Ramotswa 132kV Line CB 205 | 132 | Transmission | South | Cloudy / Rainy / Thunderstorms | 23:13 | 2.92 | SCADA/Ntoko | Trip, 87L, Three phase trip, BF, AR. On O/C Relay; HS O/C. Fault loop being L1 and L2; 3ph trip + L/O | December | High | Permanent
07/12/2023 | 20:18 | 202/23 | Ramotswa | Ramotswa - Gabsouth 132kV Line CB 205 | 132 | Transmission | South | Cloudy / Rainy / Thunderstorms | 22:32 | 2.23 | SCADA/Ntoko | Three phase trip 87L and Master trip operated. Fault loop being L1 and L2; 3ph trip + L/O | December | High | Permanent
10/12/2023 | 19:57 | 203/23 | Makoba | Makoba - Samochima 132kV line CB 105 | 132 | Transmission | North West | Cloudy / Rainy | 20:10 | 0.22 | SCADA | 3 Ph T+L/O | December | Medium | Sustained
11/12/2023 | 00:50 | 205/23 | Hydromet | Hydromet - 220kV Bus Coupler CB W10 | 220 | Transmission | North | Clear | 02:34 | 1.73 | SCADA | Pole discrepancy; tripped on closure attempt | December | High | Permanent
24/12/2023 | 23:37 | 212/23 | Orapa 2 | Orapa 2 - Serule 220kV line CB L15 | 220 | Transmission | North | Cloudy | 1:13 | 1.6 | Likokoto | Blue phase Imp E/F Zone 1; Sph T+ARC+ 3ph T +L/O | December | High | Permanent
24/12/2023 |  | 212/23 | Serule | Serule - Orapa 2 220kV line CB L15 | 220 | Transmission | North | Cloudy | 0:59 | 1.37 | Scada | Blue phase Imp E/F Zone 2; 3 ph T+ L/O | December | High | Permanent
26/12/2023 | 23:37 | 212/23 | Orapa 2 | Orapa 2 - Serule 220kV line CB L15 | 220 | Transmission | North | Cloudy | 1:13 | 1.6 | Likokoto | Blue phase Imp E/F Zone 1; Sph T+ARC+ 3ph T +L/O | December | High | Permanent
26/12/2023 |  | 212/23 | Serule | Serule - Orapa 2 220kV line CB L15 | 220 | Transmission | North | Cloudy | 0:59 | 1.37 | Scada | Blue phase Imp E/F Zone 2; 3 ph T+ L/O | December | High | Permanent
27/12/2023 | 13:32 | 214/23 | Makoba | Makoba - Samochima 132kV line CB 105 | 132 | Transmission | North West | Rain | 13:35 | 0.05 | SCADA | Zone 1, General trip, pole discrepancy; 3 phT + L/O | December | Low | Transient
27/12/2023 | 13:46 | 215/23 | Makoba | Makoba - Samochima 132kV line CB 105 | 132 | Transmission | North West | Rain | 13:54 | 0.13 | SCADA | Zone 1, General trip, pole discrepancy; 3 phT + L/O | December | Medium | Sustained
30/12/2023 |  | 217/23 | Serule | Serule - Orapa 2 220kV line CB L15 | 220 | Transmission | North | Clear | 22:04 | 0.03 | SCADA | 3ph T+L/O | December | Low | Transient
04/01/2024 | 15:13 | 003/24 | Dukwi | Dukwi - Francistown 132kV line CB 505 | 132 | Transmission | North | Cloudy | 15:36 | 0.38 | SCADA | Back up protection operated, PLC fault, PLC back up; 3 ph T + L/O | January | Medium | Sustained
05/01/2024 | 14:53 | 004/24 | Dukwi | Dukwi - Francistown 132kV line CB 505 | 132 | Transmission | North | Cloudy | 14:57 | 0.07 | SCADA/Chawilani | Back up protection operated, PLC fault, PLC back up; 3 ph T + L/O | January | Low | Transient
06/01/2024 | 22:22 | 005/24 | Orapa 2 | Orapa 2 - Serule 220kV line CB L15 | 220 | Transmission | North | Cloudy | 23:38 | 1.27 | SCADA/Likokoto | Blue phase Impedance E/F, Zone 1; Sph T+ARC+ 3 ph T+L/O | January | High | Permanent
08/01/2024 | 09:31 | 008/24 | Dukwi | Dukwi - Francistown 132kV line CB 505 | 132 | Transmission | North | Cloudy | 09:59 | 0.47 | SCADA/Molefhi | 3 ph trip, zone 1, carrier receive, zone 1 trip, PLC send main trip; 3 ph T + L/O | January | Medium | Sustained
09/01/2024 | 09:13 | 011/24 | Francistown | Francistown - Dukwi 132kV line CB 205 | 132 | Transmission | North | Cloudy | 09:18 | 0.08 | SCADA/Chawilani | No indications; 3 ph T + L/O | January | Low | Transient
11/01/2024 | 15:51 | — | Legotlhwane | Legotlhwane - Makoba 132kV line CB 305 | 132 | Transmission | North West | Cloudy | 17:34 | 1.72 | Rasefako | Earth Fault and ARC Block; 3ph T+L/O | January | High | Permanent
16/01/2024 | 18:19 | 022/24 | Gab South | Gab South- Ramotswa 132kV line CB 205 | 132 | Transmission | South | Cloudy | 18:48 | 0.48 | GABOITSIWE | 87L DIFF, HIGH SET O/C PHASE A & C; Tripped + L/O | January | Medium | Sustained
18/01/2024 | 17:05 | 025/24 | Legotlhwane | Legotlhwane - Makoba 132kV line CB 305 | 132 | Transmission | North West | Cloudy | 17:34 | 0.48 | Rasefako | MAIN PROT RELAY: PROTECTION TRIP, ARC BLOCK; 3ph T+L/O | January | Medium | Sustained
30/01/2024 | 00:37 | 036/24 | Gabs South | Gabs South - Spitskop 132kV line CB 505 | 132 | Transmission | South | Clear | 01:10 | 0.55 | SCADA/Galetshetse | Relay defective; 3 Ph T+L/O | January | High | Permanent
2024-01-03 | 11:43 | 002/24 | Thamaga – Kgale View | Kgale View - Thamaga 132kV line CB 105 | 132 | Transmission | South | Rain | 12:33 | 0.83 | SCADA/Ntoko | 2 ph T + L/O; Load loss to Karowe Mine (9.94 MW) | January | High | Permanent
2024-01-06 | 15:00 | 020/24 | Tsabong – Heuningsvlei | Heuningsvlei 132kV line CB | 132 | Transmission | North | Thunderstorm | 18:53 | 3.88 | ESKOM | Tripped; Load loss in Tsabong (2 MW) | January | High | Permanent
2024-01-11 | 12:01 | 014/24 | Thamaga – Jwaneng | Thamaga - Jwaneng 132kV line 2 CB 205 | 132 | Transmission | South | Cloudy | 13:27 | 1.43 | SCADA/MAKOKO | 3 ph Trip+L/O | January | High | Permanent
2024-01-11 | 12:01 | 014/24 | Thamaga | 220/132 Kv T2 : HV CB H20 | 132 | Transmission | South | Cloudy | 13:27 | 1.43 | SCADA/MAKOKO | Tripped | January | High | Permanent
2024-01-11 | 12:01 | 014/24 | Thamaga | 220/132 Kv T2 : LV CB 280 | 132 | Transmission | South | Cloudy | 13:27 | 1.43 | SCADA/MAKOKO | Tripped | January | High | Permanent
2024-01-11 | 12:01 | 014/24 | Thamaga – Kgale View | Kgale view 132kv line CB 405 | 132 | Transmission | South | Cloudy | 13:27 | 1.43 | SCADA/MAKOKO | 3 ph Trip+L/O | January | High | Permanent
2024-01-11 | 12:01 | 014/24 | Thamaga | 132 Kv Bus Coupler CB 230 | 132 | Transmission | South | Cloudy | 13:27 | 1.43 | SCADA/MAKOKO | Tripped | January | High | Permanent
2024-01-11 | 12:01 | 014/24 | Thamaga – Jwaneng | Jwaneng - Thamaga 132kV line 2 CB 505 | 132 | Transmission | South | Cloudy | 13:27 | 1.43 | SCADA/Mosarwe | 3 ph Trip + ARC; No load loss | January | High | Permanent
2024-01-16 | 19:31 | 023/24 | Gab South – Ramotswa | Ramotswa- Gab South 132kV line CB 205 | 132 | Transmission | South | Cloudy | 19:37 | 0.53 | SCADA/MAKOKO | 3 Ph trip + L/O; No load loss | January | High | Permanent
2024-01-26 | 22:19 | 030/24 | Thamaga | Thamaga 220/132kV T1 HV CB H10 | 132 | Transmission | South | Clear | 03:12 | 4.88 | SCADA / Galetshetse | Tripped; Intertrip latch issue | January | High | Permanent
2024-01-26 | 22:19 | 030/24 | Thamaga | Thamaga 220/132kV T1 LV CB 180 | 132 | Transmission | South | Clear | 03:12 | 4.88 | SCADA / Galetshetse | Tripped | January | High | Permanent
2024-01-26 | 22:19 | 030/24 | Thamaga – Jwaneng | Thamaga-Jwaneng 1 132kV line CB305 | 132 | Transmission | South | Clear | 03:12 | 4.88 | SCADA | 3 Ph T+L/O | January | High | Permanent
2024-01-26 | 22:19 | 030/24 | Thamaga | Thamaga 132kV B/C 230 | 132 | Transmission | South | Clear | 03:12 | 4.88 | SCADA / Galetshetse | Tripped | January | High | Permanent
2024-01-26 | 22:19 | 030/24 | Thamaga – Mmakgodumo | Thamaga - Mmakgodumo 132kV line CB 205 | 132 | Transmission | South | Clear | 03:13 | 4.9 | SCADA | 3 PhT+L/O | January | High | Permanent
2024-01-26 | 22:19 | 030/24 | Thamaga – Mmakgodumo | Mmakgodumo - Thamaga 132kV line CB 105 | 132 | Transmission | South | Clear | 03:13 | 4.9 | SCADA | 3 PhT+L/O | January | High | Permanent
2024-01-29 | 19:48 | 035/24 | Segoditshane – Dwarsberg | Segoditshane - Dwarsberg 132kV line CB905 | 132 | Transmission | South | Clear | 20:20 | 0.53 | SCADA | 3 Ph T+L/O | January | High | Permanent
2024-01-29 | 19:48 | 035/24 | Segoditshane – Dwarsberg | Dwarsberg - Segoditshane 132kV line | 132 | Transmission | South | Clear | 20:20 | 0.53 | Eskom | 3 Ph T+L/O | January | High | Permanent
2024-01-29 | 19:48 | 035/24 | Gab South – Spitskop | Gabs South - Spitskop 132kV line CB 505 | 132 | Transmission | South | Clear | 20:25 | 0.62 | SCADA/Galetshetse | 3 Ph T+L/O; Relay defective | January | High | Permanent
2024-02-11 | 07:13 | 045/24 | Rakola – Segoditshane | Rakola - Segoditshane 220kV line CB L35 | 220 | Transmission | South | Rain | 07:18 | 0.08 | SCADA/Makoko | 3ph T + L/O | February | Low | Transient
2024-02-13 | 16:43 | 046/24 | Thamaga | Thamaga - Jwaneng 1 CB 505 | 132 | Transmission | South | Rain | 19:22 | 2.65 | SCADA/Galetshetse | Bus zone trip | February | High | Permanent
2024-02-13 | 16:43 | 046/24 | Thamaga | 220/132kV T2 HV CB H20 | 132 | Transmission | South | Rain | 19:21 | 2.65 | SCADA/Galetshetse | Bus zone trip | February | High | Permanent
2024-02-13 | 16:43 | 046/24 | Thamaga | 220/132kV T2 LV CB 280 | 132 | Transmission | South | Rain | 19:21 | 2.65 | SCADA/Galetshetse | Bus zone trip | February | High | Permanent
2024-02-13 | 16:43 | 046/24 | Thamaga – Kgale View | Thamaga - Kgale View CB 405 | 132 | Transmission | South | Rain | 19:22 | 2.65 | SCADA/Galetshetse | Bus zone trip | February | High | Permanent
2024-02-13 | 16:43 | 046/24 | Thamaga | 132kV Bus Coupler CB 230 | 132 | Transmission | South | Rain | 19:20 | 2.63 | SCADA/Galetshetse | Bus zone trip | February | High | Permanent
2024-02-13 | 16:54 | 047/24 | Gab South – Ramotswa | Gab South–Ramotswa 132kV line CB 205 | 132 | Transmission | South | Rain | 17:26 | 0.53 | SCADA/Karabo | 3ph T + L/O; Differential protection | February | High | Permanent
2024-02-26 | 19:36 | 053/24 | MORP A – Serule | MORP A - Serule 220kV line CB L65 | 220 | Transmission | Central/South | Rainy | 22:21 | 2.75 | SCADA/N. Lekokoto | 3ph T + L/O | February | High | Permanent
2024-02-26 | 19:36 | 053/24 | MORP A – Serule | Serule - MORP A 220kV line CB L55 | 220 | Transmission | Central/South | Rainy | 23:18 | 3.7 | SCADA/T. Moloinaga | 3ph T + L/O; No load loss | February | High | Permanent
2024-03-02 | 02:28 | 055/24 | Mmakgodumo – Kanye | Mmakgodumo - Kanye 132kV CB 305 | 132 | Transmission | South | Clear | ARC | 0 | SCADA | 3ph T + ARC; No load loss | March | Low | Transient
2024-03-07 | 19:33 | 056/24 | Gab South – Ramotswa | Gab South–Ramotswa 132kV line CB 205 | 132 | Transmission | South | Cloudy and Windy | 20:24 | 0.85 | SCADA/Rapelang | 3ph T + L/O; High set O/C; No load loss | March | High | Permanent
2024-03-16 | 21:08 | 058.0/24 | MORP B – Isang | MORP B - Isang 400kV line CB 1L5 | 400 | Transmission | South | Clear | 21:10 | 0.03 | SCADA | 3ph T + L/O | March | Low | Transient
2024-03-16 | 21:08 | 058.0/24 | Isang – Segoditshane | Isang - Segs 220kV line CB L25 | 220 | Transmission | South | Clear | 23:08 | 2 | SCADA | 3ph T + L/O | March | High | Permanent
2024-03-16 | 21:08 | 058.0/24 | Isang – Thamaga | Isang - Thamaga 220kV line CB L55 | 220 | Transmission | South | Clear | 23:08 | 2 | SCADA | 3ph T + L/O | March | High | Permanent
2024-03-16 | 21:08 | 058.0/24 | Isang – Thamaga | Thamaga - Isang 220kV line CB L15 | 220 | Transmission | South | Clear | 23:12 | 2.07 | SCADA | Earth fault trip; 3ph T + L/O | March | High | Permanent
2024-03-16 | 21:08 | 058.0/24 | Isang – Isang Ext | Isang - Isang Ext 220kV line CBs H10 & H20 | 220 | Transmission | South | Clear | 23:21 | 2.22 | SCADA | Tripped | March | High | Permanent
2024-03-16 | 21:08 | 058.0/24 | Rakola – Isang | Rakola - Isang 220kV line CBs L15 & L45 | 220 | Transmission | South | Clear | 23:13 | 2.08 | SCADA/Karabo | B-phase E/F; 3ph T + L/O | March | High | Permanent
2024-03-16 | 21:08 | 058.2/24 | Rakola – Thamaga | Rakola - Thamaga 220kV line 2 CB L25 | 220 | Transmission | South | Clear | 01:31 | 4.38 | SCADA/Karabo | Under voltage trip | March | High | Permanent
2024-03-16 | 21:08 | 058.2/24 | Gaphatshwa – Rakola | Gaphatshwa - Rakola 132kV line CB 305 | 132 | Transmission | South | Clear | 23:30 | 2.37 | Makoko/SCADA | Under voltage trip | March | High | Permanent
2024-03-16 | 21:08 | 058.2/24 | Rakola – Gaphatshwa | Rakola - Gaphatshwa 132kV line CB 505 | 132 | Transmission | South | Clear | 23:30 | 2.37 | SCADA/Karabo | Diff trip B phase | March | High | Permanent
2024-03-16 | 21:08 | 058.2/24 | Segoditshane | Segs 220/132kV TRF 4 LV CB 480 | 132 | Transmission | South | Clear | 23:33 | 2.42 | Galetshetse/SCADA | Tripped | March | High | Permanent
2024-03-16 | 21:08 | 058.2/24 | Segoditshane – Dwarsberg | Segs - Dwarsberg 132kV line CB 905 | 132 | Transmission | South | Clear | 23:16 | 2.13 | Galetshetse/SCADA | Dist + O/C trip | March | High | Permanent
2024-03-16 | 21:08 | 058.2/24 | Phakalane – Segoditshane | Phakalane - Segs 132kV line CB 205 | 132 | Transmission | South | Clear | ARC | 0 | SCADA | 3ph T + ARC | March | Low | Transient
2024-03-16 | 21:08 | 058.3/24 | Gab South – Tlokweng | Gab South - Tlokweng 132kV line CB 905 | 132 | Transmission | South | Clear | 23:51 | 2.72 | SCADA/Mangole | Under voltage trip | March | High | Permanent
2024-03-16 | 21:08 | 058.3/24 | Tlokweng – Gab South | Tlokweng - Gab South 132kV line CB 105 | 132 | Transmission | South | Clear | 00:22 | 3.23 | SCADA/Mangole | 3ph T + L/O | March | High | Permanent
2024-03-16 | 21:08 | 058.3/24 | Tlokweng – Segoditshane | Tlokweng - Segs 132kV line CB 305 | 132 | Transmission | South | Clear | 00:24 | 3.27 | SCADA/Mangole | 3ph T + L/O | March | High | Permanent
2024-03-17 | 20:44 | 059/24 | Gaborone South – Spitskop | Gaborone South - Spitskop 132kV line CB 505 | 132 | Transmission | South | Cloudy and Windy | 21:40 | 0.93 | Karabo/SCADA | Zone 1 distance trip; 3ph T + L/O | March | High | Permanent
2024-03-18 | 22:55 | 060/24 | Lobatse – Mmakgodumo | Lobatse - Mmakgodumo 132kV Line CB 205 | 132 | Transmission | South/North | Clear | ARC | 0 | SCADA / Mangole | 1ph Trip + ARC | March | Low | Transient
2024-03-18 | 22:55 | 060/24 | Lobatse – Mmakgodumo | Mmakgodumo - Lobatse 132kV Line CB 205 | 132 | Transmission | South/North | Clear | 08:11 | 9.27 | SCADA / Mosarwe | 3ph Trip + L/O | March | High | Permanent
2024-03-29 | 18:14 | 061/24 | MORP B – Isang | MORP B - ISANG 400 kV line CB 1L5 | 400 | Transmission | Central/South | Clear | 19:31 | 1.28 | SCADA/Moalosi | 3ph T + L/O | March | High | Permanent
2024-03-29 | 18:14 | 061/24 | MORP B – Isang | ISANG - MORP B 400 kV line CB 4L5 | 400 | Transmission | Central/South | Clear | 19:31 | 1.28 | SCADA/Makoko | 3ph T + L/O | March | High | Permanent
2024-03-02 | 02:28 | 055/24 | Mmakgodumo – Kanye | Mmakgodumo - Kanye 132kV CB 305 | 132 | Transmission | South | Clear | ARC | 0 | SCADA | 3ph T + ARC; No load loss | March | Low | Transient
2024-03-07 | 19:33 | 056/24 | Gab South – Ramotswa | Gab South–Ramotswa 132kV line CB 205 | 132 | Transmission | South | Cloudy and Windy | 20:24 | 0.85 | SCADA/Rapelang | 3ph T + L/O; High set O/C; No load loss | March | High | Permanent
2024-03-16 | 21:08 | 058.0/24 | MORP B – Isang | MORP B - Isang 400kV line CB 1L5 | 400 | Transmission | South | Clear | 21:10 | 0.03 | SCADA | 3ph T + L/O | March | Low | Transient
2024-03-16 | 21:08 | 058.0/24 | Isang – Segoditshane | Isang - Segs 220kV line CB L25 | 220 | Transmission | South | Clear | 23:08 | 2 | SCADA | 3ph T + L/O | March | High | Permanent
2024-03-16 | 21:08 | 058.0/24 | Isang – Thamaga | Isang - Thamaga 220kV line CB L55 | 220 | Transmission | South | Clear | 23:08 | 2 | SCADA | 3ph T + L/O | March | High | Permanent
2024-03-16 | 21:08 | 058.0/24 | Isang – Thamaga | Thamaga - Isang 220kV line CB L15 | 220 | Transmission | South | Clear | 23:12 | 2.07 | SCADA | Earth fault trip; 3ph T + L/O | March | High | Permanent
2024-03-16 | 21:08 | 058.0/24 | Isang – Isang Ext | Isang - Isang Ext 220kV line CBs H10 & H20 | 220 | Transmission | South | Clear | 23:21 | 2.22 | SCADA | Tripped | March | High | Permanent
2024-03-16 | 21:08 | 058.0/24 | Rakola – Isang | Rakola - Isang 220kV line CBs L15 & L45 | 220 | Transmission | South | Clear | 23:13 | 2.08 | SCADA/Karabo | B-phase E/F; 3ph T + L/O | March | High | Permanent
2024-03-16 | 21:08 | 058.2/24 | Rakola – Thamaga | Rakola - Thamaga 220kV line 2 CB L25 | 220 | Transmission | South | Clear | 01:31 | 4.38 | SCADA/Karabo | Under voltage trip | March | High | Permanent
2024-03-16 | 21:08 | 058.2/24 | Gaphatshwa – Rakola | Gaphatshwa - Rakola 132kV line CB 305 | 132 | Transmission | South | Clear | 23:30 | 2.37 | Makoko/SCADA | Under voltage trip | March | High | Permanent
2024-03-16 | 21:08 | 058.2/24 | Rakola – Gaphatshwa | Rakola - Gaphatshwa 132kV line CB 505 | 132 | Transmission | South | Clear | 23:30 | 2.37 | SCADA/Karabo | Diff trip B phase | March | High | Permanent
2024-03-16 | 21:08 | 058.2/24 | Segoditshane | Segs 220/132kV TRF 4 LV CB 480 | 132 | Transmission | South | Clear | 23:33 | 2.42 | Galetshetse/SCADA | Tripped | March | High | Permanent
2024-03-16 | 21:08 | 058.2/24 | Segoditshane – Dwarsberg | Segs - Dwarsberg 132kV line CB 905 | 132 | Transmission | South | Clear | 23:16 | 2.13 | Galetshetse/SCADA | Dist + O/C trip | March | High | Permanent
2024-03-16 | 21:08 | 058.2/24 | Phakalane – Segoditshane | Phakalane - Segs 132kV line CB 205 | 132 | Transmission | South | Clear | ARC | 0 | SCADA | 3ph T + ARC | March | Low | Transient
2024-03-16 | 21:08 | 058.3/24 | Gab South – Tlokweng | Gab South - Tlokweng 132kV line CB 905 | 132 | Transmission | South | Clear | 23:51 | 2.72 | SCADA/Mangole | Under voltage trip | March | High | Permanent
2024-03-16 | 21:08 | 058.3/24 | Tlokweng – Gab South | Tlokweng - Gab South 132kV line CB 105 | 132 | Transmission | South | Clear | 00:22 | 3.23 | SCADA/Mangole | 3ph T + L/O | March | High | Permanent
2024-03-16 | 21:08 | 058.3/24 | Tlokweng – Segoditshane | Tlokweng - Segs 132kV line CB 305 | 132 | Transmission | South | Clear | 00:24 | 3.27 | SCADA/Mangole | 3ph T + L/O | March | High | Permanent
2024-03-17 | 20:44 | 059/24 | Gaborone South – Spitskop | Gaborone South - Spitskop 132kV line CB 505 | 132 | Transmission | South | Cloudy and Windy | 21:40 | 0.93 | Karabo/SCADA | Zone 1 distance trip; 3ph T + L/O | March | High | Permanent
2024-03-18 | 22:55 | 060/24 | Lobatse – Mmakgodumo | Lobatse - Mmakgodumo 132kV Line CB 205 | 132 | Transmission | South/North | Clear | ARC | 0 | SCADA / Mangole | 1ph Trip + ARC | March | Low | Transient
2024-03-18 | 22:55 | 060/24 | Lobatse – Mmakgodumo | Mmakgodumo - Lobatse 132kV Line CB 205 | 132 | Transmission | South/North | Clear | 08:11 | 9.27 | SCADA / Mosarwe | 3ph Trip + L/O | March | High | Permanent
2024-03-29 | 18:14 | 061/24 | MORP B – Isang | MORP B - ISANG 400 kV line CB 1L5 | 400 | Transmission | Central/South | Clear | 19:31 | 1.28 | SCADA/Moalosi | 3ph T + L/O | March | High | Permanent
2024-03-29 | 18:14 | 061/24 | MORP B – Isang | ISANG - MORP B 400 kV line CB 4L5 | 400 | Transmission | Central/South | Clear | 19:31 | 1.28 | SCADA/Makoko | 3ph T + L/O | March | High | Permanent
2024-05-05 | 18:57 | 072/24 | MORP B – Isang | Morupule B - Isang 400kV line CB 1L5 | 400 | Transmission | North/South | Clear | 20:13 | 1.27 | SCADA | Blue phase to ground; 3ph T + L/O | May | High | Permanent
2024-05-05 | 18:57 | 072/24 | MORP B – Isang | Isang - Morupule B 400kV line CB 4L5 | 400 | Transmission | North/South | Clear | 20:13 | 1.27 | SCADA/Makoko | Blue phase to ground; 3ph T + L/O | May | High | Permanent
2024-05-06 | 02:41 | 073/24 | MORP B – Isang | Morupule B - Isang 400kV line CB 1L5 | 400 | Transmission | North/South | Clear | 04:21 | 1.67 | SCADA | Blue phase to ground; 3ph T + L/O | May | High | Permanent
2024-05-06 | 02:41 | 073/24 | MORP B – Isang | Isang - Morupule B 400kV line CB 4L5 | 400 | Transmission | North/South | Clear | 05:18 | 2.62 | SCADA/Ntoko | Blue phase to ground; 3ph T + L/O | May | High | Permanent
2024-05-14 | 01:57 | 075/24 | MORP B – Isang | Morupule B - Isang 400kV line CB 1L5 | 400 | Transmission | North/South | Clear | 04:21 | 2.4 | SCADA | Blue phase to ground; 3ph T + L/O | May | High | Permanent
2024-05-14 | 01:57 | 075/24 | MORP B – Isang | Isang - Morupule B 400kV line CB 4L5 | 400 | Transmission | North/South | Clear | 05:18 | 3.35 | SCADA/Ntoko | Blue phase to ground; 3ph T + L/O | May | High | Permanent
2024-05-28 | 00:00 | 078/24 | Phokoje – Insukamini | Phokoje - Insukamini 400kV line CB 2L5 | 400 | Transmission | Central | Clear | 01:09 | 1.15 | SCADA/Likokoto | 3ph T + L/O | May | High | Permanent
2024-05-28 | 00:00 | 078/24 | Phokoje – Insukamini | Insukamini - Phokoje 400kV line | 400 | Transmission | Central | Clear | 01:10 | 1.17 | ZESA | 3ph T + L/O | May | High | Permanent
2024-05-31 | 07:51 | 079/24 | Gab East | Gab East T1A LV CB 1H0A | 132 | Transmission | South | Clear | 08:37 | 0.77 | SCADA/R. Galetshetse | LV REF trip | May | High | Permanent
2024-07-05 | 06:26 | 086/24 | Tlokweng – Segoditshane | Segs - Tlokweng 132kV line CB 105 | 132 | Transmission | South | Cloudy | 13:26 | 7 | SCADA/Galetshetse | 3ph T + L/O | July | High | Permanent
2024-07-05 | 06:26 | 086/24 | Tlokweng – Segoditshane | Tlokweng - Segs 132kV line CB 305 | 132 | Transmission | South | Cloudy | ARC | 0 | SCADA/Galetshetse | DIFF trip | July | Low | Transient
2024-07-12 | 20:48 | 091/24 | MORP B – Isang | MORP B - ISANG 400kV line CB 1L5 | 400 | Transmission | Central/South | Clear | 20:51 | 0.05 | SCADA/Moalosi | 3ph T + L/O; Blue phase to ground | July | Low | Transient
2024-07-12 | 20:48 | 091/24 | MORP B – Isang | ISANG - MORP B 400kV line CB 4L5 | 400 | Transmission | Central/South | Clear | 20:51 | 0.05 | SCADA/Rapelang | 3ph T + L/O | July | Low | Transient
2024-07-20 | 10:17 | 092/24 | Legotlhwane – Motheo | Legotlhwane - Motheo 132kV CB 205 | 132 | Transmission | North West | Clear | 14:50 | 4.55 | SCADA/Mosala | Load loss to Ghanzi (3 MW) & Motheo Mine (4 MW) | July | High | Permanent
2024-07-23 | 11:35 | 094/24 | Thamaga – Jwaneng | Thamaga - Jwaneng 132kV line 2 CB 505 | 132 | Transmission | South | Clear | 12:07 | 0.53 | SCADA/Gaboitsiwe | 3ph T + L/O | July | High | Permanent
2024-07-23 | 11:35 | 094/24 | Thamaga – Jwaneng | Jwaneng - Thamaga 132kV line 2 CB 205 | 132 | Transmission | South | Clear | 12:08 | 0.55 | SCADA/Charles | 3ph T + ARC | July | High | Permanent
2024-07-24 | 15:03 | 094/24 | Letlhakane – Morupule B | Letlhakane - Morupule B 400kV line CB L15 | 400 | Transmission | North | Clear | 16:20 | 1.28 | SCADA/Makoko | 3ph T + L/O | July | High | Permanent
2024-07-24 | 15:03 | 094/24 | Letlhakane – Morupule B | Morupule B - Letlhakane 400kV line CB L25 | 400 | Transmission | North | Clear | 16:20 | 1.28 | SCADA/Ntoko | 3ph T + L/O | July | High | Permanent
2024-09-02 | 08:20 | 100/24 | MORP B – Isang | MORP B - ISANG 400kV line CB 1L5 | 400 | Transmission | Central/South | Clear | 10:41 | 2.35 | SCADA/Moalosi | 3ph T + L/O; L1-N fault | September | High | Permanent
2024-09-02 | 08:20 | 100/24 | MORP B – Isang | ISANG - MORP B 400kV line CB 4L5 | 400 | Transmission | Central/South | Clear | 10:41 | 2.35 | SCADA/Rapelang | 3ph T + L/O | September | High | Permanent
2024-09-04 | 05:58 | 102/24 | Tlokweng | Tlokweng T1 HV CB 110 | 132 | Transmission | South | Clear | 17:45 | 11.78 | SCADA/Galetshetse | Master trip, backup trip | September | High | Permanent
2024-09-12 | 07:51 | 103/24 | Jwaneng | Jwaneng T8 HV CB | 132 | Transmission | South | Clear | 08:54 | 1.05 | SCADA/Mosarwe | Diff relay trip; Load loss (7.5 MW) | September | High | Permanent
2024-09-14 | 00:56 | 104/24 | Orapa | Orapa 220/33kV T1 HV CB H10 | 220 | Transmission | Central | Clear | 11:19 | 50.38 | SCADA/Likokoto | Master trip, REF trip; Load loss (3 MW) | September | High | Permanent
2024-09-14 | 00:56 | 104/24 | Orapa | Orapa 220/33kV T1 LV CB 1H0 | 220 | Transmission | Central | Clear | 11:19 | 50.38 | SCADA/Likokoto | Tripped | September | High | Permanent
2024-09-15 | 08:01 | 105/24 | Zone 5 – Bosetu | Zone 5 - Bosetu 132kV line CB 105 | 132 | Transmission | North West | Clear | 12:28 | 4.45 | SCADA/Mosala | Bus zone trip; Load loss (8.31 MW) | September | High | Permanent
2024-09-15 | 08:01 | 105/24 | Zone 5 – Bosetu | T1 HV CB 110 | 132 | Transmission | North West | Clear | 12:31 | 4.5 | SCADA/Mosala | Tripped | September | High | Permanent
2024-09-15 | 08:01 | 105/24 | Zone 5 – Bosetu | T2 HV CB 210 | 132 | Transmission | North West | Clear | 12:32 | 4.52 | SCADA/Mosala | Tripped | September | High | Permanent
2024-09-20 | 05:43 | 106/24 | MORP B – Isang | MORP B - ISANG 400kV line CB 1L5 | 400 | Transmission | Central/South | Clear | 05:46 | 0.05 | SCADA/Moalosi | 3ph T + L/O | September | Low | Transient
2024-09-20 | 00:56 | 107/24 | Orapa | Orapa 220/33kV T1 HV CB H10 | 220 | Transmission | Central | Clear | 11:19 | 50.38 | SCADA/Likokoto | Duplicate of 104/24 | September | High | Permanent
2024-09-27 | 11:51 | 107/24 | Segoditshane – Dwarsberg | SEGS - DWARS 132kV line CB 905 | 132 | Transmission | South | Clear | 12:00 | 0.15 | SCADA/Ntoko | 3ph T + L/O | September | Medium | Sustained
2024-09-27 | 11:51 | 107/24 | Segoditshane – Dwarsberg | DWARS - SEGS 132kV line CB | 132 | Transmission | South | Clear | 11:58 | 0.12 | Eskom | 3ph T + L/O | September | Medium | Sustained
2024-09-28 | 13:25 | 108/24 | Rakola – Gaphatshwa | Rakola - Gaphatshwa 132kV line CB 505 | 132 | Transmission | South | Cloudy | 14:58 | 1.55 | SCADA/Ntoko | 3ph T + L/O; Load loss (14.64 MW) | September | High | Permanent
2024-09-30 | 20:25 | 110/24 | Mmakgodumo – Lobatse | Mmakgodumo - Lobatse 132kV line CB 205 | 132 | Transmission | South | Cloudy | 20:27 | 0.03 | SCADA | White phase trip; 3ph T + L/O | September | Low | Transient
2024-09-30 | 20:25 | 110/24 | Lobatse – Mmakgodumo | Lobatse - Mmakgodumo 132kV line CB 205 | 132 | Transmission | South | Cloudy | 20:28 | 0.05 | SCADA | B/U E/F & O/C trip | September | Low | Transient
2024-10-11 | 16:21 | 112/24 | Jwaneng | Jwaneng T8 HV CB 110 | 132 | Transmission | South | Clear | 17:17 | 0.93 | SCADA | Diff trip (Phase C); Load loss (5.5 MW) | October | High | Permanent
2024-10-18 | 14:11 | 115/24 | Segoditshane – Airport Road | Segs - Airport Road 132kV Line CB 205 | 132 | Transmission | South | Clear | 14:56 | 0.75 | SCADA/Galetshetse | 3ph T + L/O; No load loss | October | High | Permanent
2024-10-27 | 18:45 | 119/24 | Dukwi – Sua Pan | Dukwi - Sua 132kV line CB 305 | 132 | Transmission | North | Cloudy | 19:34 | 0.82 | SCADA | 3ph T + L/O; loud noise reported | October | High | Permanent
2024-11-08 | 14:57 | 127/24 | Makoba – Samochima | Makoba - Samochima 132kV line CB 105 | 132 | Transmission | North | Rainy | 15:03 | 0.1 | SCADA | 3ph T + L/O; Load loss (3.2 MW) | November | Medium | Sustained
2024-11-09 | 15:48 | 132/24 | Maun | Maun T2 HV CB 210 & LV CB 2T0 | 132 | Transmission | North | Cloudy | 18:19 | 2.52 | SCADA | E/F, Master trip; No load loss | November | High | Permanent
2024-11-09 | 16:52 | 133/24 | Makoba – Samochima | Makoba - Samochima 132kV line CB 105 | 132 | Transmission | North | Cloudy & Windy | 16:55 | 0.05 | SCADA | 3ph T + L/O; Load loss (3.2 MW) | November | Low | Transient
2024-11-09 | 16:52 | 133/24 | Makoba – Samochima | Samochima - Makoba 132kV line CB 305 | 132 | Transmission | North | Cloudy & Windy | 16:55 | 0.05 | SCADA | 3ph T + L/O | November | Low | Transient
2024-11-09 | 17:04 | 134/24 | Makoba – Samochima | Makoba - Samochima 132kV line CB 105 | 132 | Transmission | North | Cloudy & Windy | 18:07 | 1.05 | SCADA | 3ph T + L/O; Load loss (3.2 MW) | November | High | Permanent
2024-11-10 | 22:24 | 136/24 | Makoba – Samochima | Makoba - Samochima 132kV line CB 105 | 132 | Transmission | North | Rainy | 22:39 | 0.25 | SCADA | 3ph T + L/O; Load loss (3.2 MW) | November | Medium | Sustained
2024-11-10 | 23:36 | 137/24 | Gaphatshwa | Gaphatshwa T2 HV CB 610 | 132 | Transmission | South | Clear | 1:03 | 1.45 | SCADA/Galetshetse | Tripped; Load loss (4 MW) | November | High | Permanent
2024-11-12 | 05:09 | 138/24 | Dukwi – Mawana | Dukwi - Mawana 132kV line CB 105 | 132 | Transmission | North | Cloudy | 06:03 | 1.1 | SCADA | 3ph T + L/O; Load loss (7 MW) | November | High | Permanent
2024-11-12 | 05:09 | 138/24 | Mawana – Dukwi | Mawana - Dukwi 132kV line CB 105 | 132 | Transmission | North | Cloudy | ARC | 0 | SCARA | 3ph T + ARC | November | Low | Transient
2024-11-12 | 11:03 | 141/24 | Morupule B – Phokoje | Morupule B - Phokoje 400kV Line CB 3L5 | 400 | Transmission | Central | Rainy | 13:15 | 2.2 | SCADA /Moloinoga | DTTS ,DTTR ,Master trip | November | High | Permanent
2024-11-12 | 11:03 | 141/24 | Morupule B – Phokoje | Phokoje - Morupule B 400kV Line CB 1L5 | 400 | Transmission | Central | Rainy | 13:14 | 2.18 | SCADA/Likokotlo | DTTR ,Phase RWB Trip | November | High | Permanent
2024-11-12 | 11:03 | 141/24 | Morupule B | Morupule B Busbar CB 1RO | 400 | Transmission | Central | Rainy | 13:16 | 2.22 | SCADA /Moloinoga | Bus zone trip | November | High | Permanent
2024-11-12 | 11:03 | 141/24 | Morupule B | Morupule B Buscoupler CB 2WO | 400 | Transmission | Central | Rainy | 13:06 | 2.05 | SCADA /Moloinoga | Bus zone B trip | November | High | Permanent
2024-11-12 | 11:03 | 141/24 | Morupule B | Morupule B Generator 1 | 400 | Transmission | Central | Rainy | 13:29 | 2.43 | SCADA | Tripped | November | High | Permanent
2024-11-12 | 11:03 | 141/24 | Morupule B | Morupule B 400/220kV Station Transformer 1 CB 1TO | 400 | Transmission | Central | Rainy | 13:35 | 2.53 | SCADA /Moloinoga | Bus zone trip | November | High | Permanent
2024-11-13 | 11:06 | 142/24 | MORP B – Isang | ISANG - MORP B 400kV line CB 4L5 | 400 | Transmission | Central | Cloudy | 12:40 | 1.57 | SCADA/R. Galetshetse | 3ph T + L/O | November | High | Permanent
2024-11-13 | 21:43 | 143/24 | MORP B – Isang | ISANG - MORP B 400kV line CB 4L5 | 400 | Transmission | Central | Cloudy | 23:14 | 1.52 | SCADA/SELEI | 3ph T + L/O (during protection test) | November | High | Permanent
2024-11-22 | 21:23 | 145/24 | Phokoje – Serule | Phokoje - Serule 220kV Line CB L35 | 220 | Transmission | Central | Cloudy | 21:32 | 0.15 | SCADA | Blue phase to neutral | November | Medium | Sustained
2024-11-22 | 21:23 | 145/24 | Phokoje – Serule | Serule - Phokoje 220kV Line CB L95 | 220 | Transmission | Central | Cloudy | 21:55 | 0.53 | SCADA/D. Sekgatlhola | Blue phase to neutral | November | High | Permanent
2024-11-24 | 00:41 | 147/24 | Morupule B | Morupule B Unit 4 | Misc | Transmission | Central | Cloudy | 01:08 | 0.45 | SCADA | PA Fluctuations | November | Medium | Sustained
2024-11-24 | 01:36 | 148/24 | Makoba – Legotlhwane | Makoba - Legotlhwane 132kV Line CB 105 | 132 | Transmission | North | Cloudy | 01:39 | 0.05 | SCADA | 3ph T + L/O; Load loss (2.5 MW) | November | Low | Transient
2024-11-24 | 18:21 | 150/24 | Rakola – Molepolole | Rakola - Molepolole 132kV CB 205 | 132 | Transmission | South | Cloudy | 18:23 | 0.03 | SCADA /Sekgatlhola | 3ph T + L/O | November | Low | Transient
2024-11-24 | 20:16 | 152/24 | Phokoje – Insukamini | Phokoje - Insukamini 400kV Line CB 2L5 | 400 | Transmission | Central | Cloudy | 21:21 | 1.08 | SCADA | 3ph T + L/O | November | High | Permanent
2024-11-24 | 20:16 | 152/24 | Phokoje – Insukamini | Insukamini - Phokoje 400kV line | 400 | Transmission | Central | Cloudy | 21:35 | 1.32 | SCADA | 3ph T + L/O | November | High | Permanent
2024-11-26 | 14:57 | 159/24 | Makoba – Samochima | Samochima - Makoba 132kV line CB 305 | 132 | Transmission | North | Rain & Thunder | 14:58 | 0.02 | SCADA/Rasefako | 3ph T + L/O; Load loss (2.4 MW) | November | Low | Transient
2024-11-26 | 18:59 | 120/24 | Phokoje – Insukamini | Phokoje - Insukamini 400kV line CB 2L5 | 400 | Transmission | North | Clear | 20:23 | 1.4 | SCADA | 3ph T + L/O | November | High | Permanent
2024-11-26 | 18:59 | 120/24 | Phokoje – Insukamini | Insukamini - Phokoje 400kV line | 400 | Transmission | North | Clear | NIL | 0 | ZESA | 3ph T + L/O | November | Low | Transient
2024-11-26 | 19:32 | 120/24 | Phokoje – Selebi-Phikwe | Phokoje - Selebi-Phikwe 220kV line CB L25 | 220 | Transmission | Central | Clear | 20:15 | 0.72 | SCADA/Likokoto | 3ph T + L/O | November | High | Permanent
2024-11-26 | 19:32 | 120/24 | Phokoje – Selebi-Phikwe | Selebi-Phikwe - Phokoje 220kV line CB L15 | 220 | Transmission | Central | Clear | 20:15 | 0.72 | SCADA/Ntoko | 3ph T + L/O | November | High | Permanent
2024-11-27 | 14:55 | 131/24 | Dukwi – Sua Pan | Dukwi - Sua Pan 132kV line CB 305 | 132 | Transmission | North | Cloudy | 14:56 | 0.02 | SCADA | 3ph T + L/O; Load loss (4 MW) | November | Low | Transient
2024-11-27 | 23:13 | 121/24 | Dukwi – Mowana | Dukwi - Mowana 132kV line CB 205 | 132 | Transmission | North | Cloudy & Windy | 5:28 | 6.25 | Molefhi | 3ph T + L/O; Load loss (3 MW) | November | High | Permanent
2024-11-08 | 13:32 | 125/24 | Serule – Orapa 2 | Serule - Orapa 2 220kV line CB L15 | 220 | Transmission | North | Cloudy | 13:35 | 0.05 | SCADA | 3 Ph T+L/O | November | Low | Transient
2024-11-08 | 13:32 | 125/24 | Orapa 2 – Serule | Orapa 2 - Serule 220kV line CB L15 | 220 | Transmission | North | Cloudy | 14:25 | 0.88 | Tsenang | 3 Ph T+L/O | November | High | Permanent
2024-11-12 | 06:30 | 139/24 | S-Phikwe (Bobonong 66kV) | 220/66kV T6: HV CB H60 & LV CB 110 | 132 | Transmission | South | Clear | 11:38 | 5.13 | SCADA/Galetshetse | TX restored after CSS removed shield wire on Bobonong 66kV line; Load loss (9 MW) | November | High | Permanent
2024-12-01 | 15:38 | 161/24 | S/Phikwe – Phokoje 2 | S/Phikwe - Phokoje 2 220kV Line CB L15 | 220 | Transmission | South | Clear | 20:08 | 4.5 | SCADA / Likokotlo | O/C; Load loss to S/Phikwe, WUC, BCL (25 MW) | December | High | Permanent
2024-12-01 | 15:38 | 161/24 | Phokoje – S/Phikwe 2 | Phokoje - S/Phikwe 2 220kV Line CB L45 | 220 | Transmission | South | Clear | 20:11 | 4.55 | SCADA / Likokotlo | Did not trip initially; later closed | December | High | Permanent
2024-12-01 | 15:38 | 161/24 | S/Phikwe | S/Phikwe 220/11kV Transformer 1 HV CB H20 | 220 | Transmission | South | Clear | 20:09 | 4.52 | SCADA / Likokotlo | REF Start, Master trip | December | High | Permanent
2024-12-01 | 15:38 | 161/24 | S/Phikwe | S/Phikwe 220/11kV Transformer 3 HV CB H30 | 220 | Transmission | South | Clear | 20:11 | 4.55 | SCADA / Likokotlo | REF Start | December | High | Permanent
2024-12-01 | 15:38 | 161/24 | S/Phikwe | S/Phikwe 220/66kV Transformer 5 HV CB H50 | 220 | Transmission | South | Clear | 20:10 | 4.53 | SCADA / Likokotlo | HV O/C & E/F trip | December | High | Permanent
2024-12-01 | 15:38 | 161/24 | S/Phikwe | S/Phikwe 220/66kV Transformer 6 HV CB H60 | 220 | Transmission | South | Clear | 20:09 | 4.52 | SCADA / Likokotlo | REF harmonic block, Inter trip receive | December | High | Permanent
2024-12-03 | 08:42 | 162/24 | Phokoje – Serule | Phokoje - Serule 220kV line CB L55 | 220 | Transmission | Central | Clear | 08:48 | 0.1 | SCADA | 3ph T + L/O | December | Medium | Sustained
2024-12-03 | 08:42 | 162/24 | Serule – Phokoje | Serule - Phokoje 220kV line CB L65 | 220 | Transmission | Central | Clear | 08:48 | 0.1 | SCADA | 3ph T + L/O | December | Medium | Sustained
2024-12-06 | 02:18 | 163/24 | S/Phikwe – Phokoje 2 | S/Phikwe - Phokoje 2 220kV Line CB L15 | 220 | Transmission | Central | Clear | 03:26 | 1.13 | SCADA / Likokotlo | Zone 1, Phase C-G, SOTF; 3ph Trip+L/O | December | High | Permanent
2024-12-06 | 02:18 | 163/24 | S/Phikwe | S/Phikwe 220/66kV Transformer 5 HV CB H50 | 220 | Transmission | Central | Clear | 04:12 | 1.9 | SCADA / Boiditswe | — | December | High | Permanent
2024-12-06 | 02:18 | 163/24 | S/Phikwe | S/Phikwe 220/66kV Transformer 6 HV CB H60 | 220 | Transmission | Central | Clear | 07:18 | 5 | SCADA / Boiditswe | — | December | High | Permanent
2024-12-10 | 16:08 | 165/24 | Ramotswa – Woodhall | Ramotswa - Woodhall 132kV Line CB 105 | 132 | Transmission | South | Cloudy | 16:09 | 0.02 | SCADA / Kaloso | 3ph trip + L/O | December | Low | Transient
2024-12-10 | 18:02 | 167/24 | Segs – Dwaarsberg | Segs - Dwaarsberg 132kV Line CB 905 | 132 | Transmission | South | Clear | 18:18 | 0.27 | SCADA | 3ph trip + L/O | December | Medium | Sustained
2024-12-10 | 18:02 | 167/24 | Gabsouth – Spitskop | Gabsouth - Spitskop 132kV Line CB 505 | 132 | Transmission | South | Clear | 19:17 | 1.25 | SCADA / Rapelang | 3ph trip + L/O | December | High | Permanent
2024-12-10 | 22:35 | 166/24 | Maun | Maun 132/11kV T1 LV CB 1TO | 132 | Transmission | North/West | Clear | 23:57 | 1.37 | SCADA / Rasefako | Due to CSS feeders | December | High | Permanent
2024-12-13 | 06:53 | 070/24 | Morupule A – Isang | Morupule A - Isang 220kV line CB 1L5 | 220 | Transmission | North/South | Clear | 06:57 | 0.07 | SCADA | 3ph T + L/O | December | Low | Transient
2024-12-13 | 06:53 | 070/24 | Isang – Morupule A | Isang - Morupule A 220kV line CB 1L5 | 220 | Transmission | North/South | Clear | 06:57 | 0.07 | SCADA | 3ph T + L/O | December | Low | Transient
2024-12-13 | 20:22 | 170/24 | Phokoje – Insukamini | Phokoje - Insukamini 400kV Line CB 2L5 | 400 | Transmission | Central | Cloudy | 20:29 | 0.12 | SCADA | 3ph T + L/O; Z1 operated | December | Medium | Sustained
2024-12-13 | 20:22 | 170/24 | Insukamini – Phokoje | Insukamini - Phokoje 400kV Line CB 2L5 | 400 | Transmission | Central | Cloudy | 21:00 | 0.63 | SCADA | 3ph T + L/O | December | High | Permanent
2024-12-15 | 17:37 | 172/24 | Jwaneng – Thamaga | Jwaneng - Thamaga 132kV Line 1 CB 105 | 132 | Transmission | South | Rainy | 17:37 | 0 | SCADA | 3Ph trip +ARC; No load loss | December | Low | Transient
2024-12-16 | 07:43 | 074/24 | Morupule A – Serule | Morupule A - Serule 220kV line CB L55 | 220 | Transmission | Central | Cloudy | 08:58 | 1.25 | SCADA / Moalosi | 3ph T + L/O; Z1, Z2 trips; Distance to fault = 21.71 km; Spring found discharged | December | High | Permanent
2024-12-16 | 07:43 | 074/24 | Serule – Morupule A | Serule - Morupule A 220kV line CB L65 | 220 | Transmission | Central | Cloudy | 08:59 | 1.27 | SCADA / Sekgatlhola | 3ph T + L/O | December | High | Permanent
2024-12-16 | 14:15 | 075/24 | Francistown Main – Dukwe | Francistown Main - Dukwe 132kV line CB 205 | 132 | Transmission | North | Cloudy | 14:15 | 0 | SCADA / Chabalala | 3ph trip + ARC; Zone 1; Distance to fault = 43.1 km; No load loss | December | Low | Transient
2024-12-17 | 22:36 | 174/24 | Orapa 2 | Orapa 2 220/33kV Transformer 1 HV CB H10 | 220 | Transmission | North | Rainy | 05:10 | 6.57 | SCADA / Tsenang | Load loss to Debswana; Mine Feeder 1 tripped on O/C, Feeder 2 on E/F | December | High | Permanent
2024-12-20 | 15:16 | 180/24 | Mawana – Maun | Mawana - Maun 132kV line CB 305 | 132 | Transmission | North | Rainy | 15:48 | 0.53 | SCADA / Mosala | 3ph T + L/O; Load loss to Maun Substation (10.9 MW) | December | High | Permanent
2024-12-20 | 15:16 | 180/24 | Maun – Mawana | Maun - Mawana 132kV line CB 105 | 132 | Transmission | North | Rainy | 15:27 | 0.18 | SCADA / Mosala | 3ph T + L/O | December | Medium | Sustained
2024-12-23 | 03:20 | 182/24 | Morupule B – Isang | Morupule B - Isang 400kV line CB 1L5 | 400 | Transmission | North/South | Rainy | 03:26 | 0.1 | SCADA / Galetshetse | 3ph T + L/O | December | Medium | Sustained
2024-12-23 | 03:20 | 182/24 | Isang – Morupule B | Isang - Morupule B 400kV line CB 4L5 | 400 | Transmission | North/South | Rainy | 05:06 | 1.77 | SCADA / Galetshetse | White phase to ground; 400/220kV T2&3 switched out for restoration | December | High | Permanent
2024-12-24 | 15:20 | 183/24 | Legotlhwane – Makoba | Legotlhwane - Makoba 132kV line CB 305 | 132 | Transmission | North/West | Rainy | 15:22 | 0.03 | SCADA | 3ph T + L/O; Load loss (3.8 MW) to Makoba and Samochima areas | December | Low | Transient
2024-12-24 | 15:20 | 183/24 | Makoba – Legotlhwane | Makoba - Legotlhwane 132kV line CB 305 | 132 | Transmission | North/West | Rainy | 15:21 | 0.02 | SCADA | 3ph T + L/O | December | Low | Transient
2024-12-28 | 22:26 | 185/24 | Phokoje – Serule | Phokoje - Serule 220kV Line CB L35 | 220 | Transmission | North | Rainy | 23:30 | 1.07 | SCADA / Sekgatlhola | 3ph trip + L/O | December | High | Permanent
2024-12-31 | 18:15 | 188/24 | Woodhall | Woodhall T1A: 132kV CB 110 | 132 | Transmission | South | Rainy | 18:57 | 0.7 | SCADA / Charles | STANDBY E/F HIGH SET; Load loss to Lobatse (5 MW) | December | High | Permanent
2024-12-31 | 18:15 | 188/24 | Woodhall | Woodhall T4: 132kV CB 410 | 132 | Transmission | South | Rainy | 19:11 | 0.92 | SCADA | CB TRIP; Load loss to Lobatse (7 MW) | December | High | Permanent
2024-12-31 | 18:15 | 188/24 | Woodhall – Lobatse | Woodhall - Lobatse 132kV Line CB 105 | 132 | Transmission | South | Rainy | 18:40 | 0.42 | SCADA | — | December | Medium | Sustained
2024-12-31 | 18:15 | 188/24 | Woodhall – Ramotswa | Woodhall - Ramotswa 132kV Line CB 205 | 132 | Transmission | South | Rainy | 19:23 | 1.13 | SCADA | — | December | High | Permanent
2025-01-01 | 15:21 | 003/25 | Segs – Dwaarsberg | Segs - Dwaarsberg 132kV Line CB 905 | 132 | Transmission | South | Clear | 15:24 | 0.05 | SCADA | Zone 2 trip; 3ph T + L/O | January | Low | Transient
2025-01-05 | 07:17 | 104/25 | Gab South – Dwaarsberg | Gab South - Dwaarsberg 132kV Line CB 905 | 132 | Transmission | South | Cloudy | 17:14 | 9.95 | SCADA / Kaloso | Zone 1 trip, L1-N fault; Line patrol found no fault | January | High | Permanent
2025-01-05 | 07:17 | 104/25 | Dwaarsberg – Gab South | Dwaarsberg - Gab South 132kV Line CB 305 | 132 | Transmission | South | Cloudy | 17:14 | 9.95 | Eskom | Zone 3 trip; 3ph T + L/O | January | High | Permanent
2025-01-11 | 16:34 | 008/25 | Ghantsi – Omaere | Ghantsi - Omaere 132kV line CB 105 | 132 | Transmission | South | Cloudy | 16:35 | 0.02 | SCADA | White phase Impedance E/F protection; 3ph T+L/O | January | Low | Transient
2025-01-13 | 14:15 | 010/25 | Francistown Main – Dukwe | Francistown Main - Dukwe 132kV line CB 105 | 132 | Transmission | North | Clear | 14:15 | 0 | SCADA / Chabalala | 3ph trip + ARC; Zone 1; Distance to fault = 43.1 km; No load loss | January | Low | Transient
2025-01-13 | 14:21 | 010/25 | Orapa 2 | Orapa 2 220/33kV T1 HV & LV CBs | 220 | Transmission | North | Rainy | 15:32 | 1.18 | SCADA / Tsenang | MASTER TRIP, MV STANDBY E/F; Load loss to Letlhakane mine/village (7 MW) | January | High | Permanent
2025-01-15 | 17:37 | 012/25 | Jwaneng – Thamaga | Jwaneng - Thamaga 132kV Line 1 CB 105 | 132 | Transmission | South | Rainy | 17:37 | 0 | SCADA | 3Ph trip +ARC; No load loss | January | Low | Transient
2025-01-15 | 22:35 | 013/25 | Makoba | Makoba T2 HV & LV CBs | 132 | Transmission | Northwest | Cloudy | 04:10 | 4.77 | SCADA / Rasefako | HV Bus zone trip, LV B/Z trip; Load loss 1.21 MW; Restored via NOP bus section | January | High | Permanent
2025-01-16 | 16:36 | 014/25 | Mmakgodumo – Lobatse | Mmakgodumo - Lobatse 132kV line CB 205 | 132 | Transmission | South | Rainy | 16:36 | 0 | SCADA | 3Ph T + ARC; R W B phase trip, VT operated | January | Low | Transient
2025-01-16 | 16:36 | 014/25 | Lobatse – Mmakgodumo | Lobatse - Mmakgodumo 132kV line CB 205 | 132 | Transmission | South | Rainy | 16:36 | 0 | SCADA | BU O/C & E/F trip, Diff trip; 3 ph T + ARC | January | Low | Transient
2025-01-21 | 15:19 | 016/25 | Tsabong – Heuning Vlei | Tsabong - Heuning Vlei 132kV line CB 105 | 132 | Transmission | South | Clear | 22:39 | 7.33 | Mosarwe | Zone 1, Phase A-G; suspected CSS feeder fault; Load loss 3 MW | January | High | Permanent
2025-01-21 | 19:31 | 018/25 | Orapa 1 – Orapa 2 | Orapa 1 - Orapa 2 220kV line CB L15 | 220 | Transmission | North | Cloudy | 21:03 | 1.53 | SCADA / Tsenang | Zone 1, 50/51 trip; Fault loop A-C; Load loss 28 MW | January | High | Permanent
2025-01-25 | 21:04 | 020/25 | Phokoje – Serule | Phokoje - Serule 220kV line CB L35 | 220 | Transmission | Central | Clear | 22:08 | 1.07 | SCADA / Likokoto | Master trip, DTTS, I/T send; 3ph T + L/O | January | High | Permanent
2025-01-25 | 21:04 | 020/25 | Serule – Phokoje | Serule - Phokoje 220kV line CB L95 | 220 | Transmission | Central | Clear | 23:31 | 2.45 | SCADA / Moalosi | O/C & E/F relay; Master trip; 3ph T + L/O | January | High | Permanent
2025-01-27 | 04:24 | 021/25 | Phokoje – Matimba | Phokoje - Matimba 400kV Line CB 3L5 | 400 | Transmission | Central | Clear | 05:19 | 0.92 | SCADA / Lekokotlo | Direction E/F Trip, DTTS, Lockout; 3Ph trip +L/O | January | High | Permanent
2025-01-27 | 04:24 | 021/25 | Matimba – Phokoje | Matimba - Phokoje 400kV Line CB 1L5 | 400 | Transmission | Central | Clear | 04:35 | 0.18 | SCADA / Eskom | Red Phase to Ground; Distance to fault 132km | January | Medium | Sustained
2025-01-27 | 04:24 | 021/25 | Phokoje – Insukamini | Phokoje - Insukamini 400kV Line CB 2L5 | 400 | Transmission | Central | Clear | 05:22 | 0.97 | SCADA / Lekokotlo | Master trip, DTTS, DTTR; 3Ph trip +L/O | January | High | Permanent
2025-01-27 | 04:24 | 021/25 | Insukamini – Phokoje | Insukamini - Phokoje 400kV Line CB 1105 | 400 | Transmission | Central | Clear | 05:25 | 1.02 | SCADA / ZESA | 3Ph trip +L/O | January | High | Permanent
2025-01-27 | 22:57 | 020/25 | Gabsouth – Spitskop | Gabsouth - Spitskop 132kV Line CB 505 | 132 | Transmission | South | Clear | 00:19 | 1.37 | SCADA / Kaloso | 3Ph trip + L/O | January | High | Permanent
2025-01-28 | 23:25 | 022/25 | Morupule A | Morupule A 220kV Bus Coupler CB W10 | 220 | Transmission | Central | Clear | 00:34 | 1.15 | SCADA / Moalosi | Protection operated | January | High | Permanent
2025-01-28 | 23:25 | 022/25 | Morupule A – Serule | Morupule A - Serule 220kV line CB L55 | 220 | Transmission | Central | Clear | 01:03 | 1.63 | SCADA / Moalosi | 3ph T + L/O; Distance to fault = 17.58 km | January | High | Permanent
2025-01-28 | 23:25 | 022/25 | Serule – Morupule A | Serule - Morupule A 220kV line CB L65 | 220 | Transmission | Central | Clear | 01:00 | 1.58 | SCADA / Likokoto | 3ph T + L/O | January | High | Permanent
2025-01-30 | 22:43 | 023/25 | Morupule A – Isang | Morupule A - Isang 220kV line 2 CB L25 | 220 | Transmission | North/South | Clear | 22:58 | 0.25 | SCADA | Zone 1 trip, carrier aided; 3ph T + L/O | January | Medium | Sustained
2025-02-07 | 18:29 | 030/25 | Rakola – Gaphatshwa | Rakola - Gaphatshwa 132kV line CB 505 | 132 | Transmission | South | Cloudy | 18:41 | 0.2 | SCADA | Backup & Instantaneous trip; Load loss 14.64 MW | February | Medium | Sustained
2025-02-10 | 09:22 | 067/25 | Tlokweng | Tlokweng 132/11kV T2 HV CB 210 | 132 | Transmission | Tlokweng | Cloudy | 18:30 | 9.13 | SCADA / Galetshetse | Winding 1 & 2 trip, DIFF trip; No load loss | February | High | Permanent
2025-02-11 | 15:21 | 041/25 | Legotlhwane – Makoba | Legotlhwane - Makoba 132kV line CB 305 | 132 | Transmission | Northwest | Cloudy | 15:22 | 0.02 | SCADA | 3ph T + ARC; Load loss (2.4 MW Makoba, 3 MW Samochima) | February | Low | Transient
2025-02-14 | 00:02 | 042/25 | Legotlhwane – Mawana | Legotlhwane - Mawana 220kV Line CB L15 | 220 | Transmission | Northwest | Rain | 00:56 | 0.9 | SCADA / Mosala | Diff trip, E/F, ARC; Load loss: Boseto (10.5 MW), Zone 5 (10.5 MW), Motheo Mine (10 MW) | February | High | Permanent
2025-02-14 | 00:02 | 042/25 | Mawana – Legotlhwane | Mawana - Legotlhwane 220kV Line CB 25 | 220 | Transmission | Northwest | Rain | 00:56 | 0.9 | SCADA / Mosala | Imp Z1/Z2/Z4 trip, IDMT O/C, Broken conductor start | February | High | Permanent
2025-02-14 | 00:02 | 042/25 | Mawana | Mawana 220/132kV Transformer 2 HV CB H20 | 220 | Transmission | Northwest | Rain | 00:56 | 0.9 | SCADA / Mosala | Diff trip, HV Low E/F Start | February | High | Permanent
2025-02-14 | 00:02 | 042/25 | Mawana | Mawana 220/132kV Transformer 2 LV CB 280 | 132 | Transmission | Northwest | Rain | 00:56 | 0.9 | SCADA / Mosala | Master trip, LV Standby E/F Start, HV CB TCS trip | February | High | Permanent
2025-02-14 | 01:55 | 043/25 | Orapa 2 – Serule | Orapa 2 - Serule 220kV Line CB L15 | 220 | Transmission | North | Rain | 03:04 | 1.15 | SCADA / Tsenang | Main 2: SOTF, Phase C-G, Distance to fault = 24.0 km | February | High | Permanent
2025-02-16 | 22:48 | 048/25 | Thamaga – Isang | Thamaga - Isang 220kV Line Reactor CB R10 | 220 | Transmission | South | Rain | 00:49 | 2.02 | SCADA / Rapelang | B/UP Protection Relay: Protection trip, B/UP trip | February | High | Permanent
2025-02-17 | 04:56 | 050/25 | Thamaga – Isang | Thamaga - Isang 220kV Line Reactor CB R10 | 220 | Transmission | South | Rain | 05:03 | 0.12 | SCADA | Tripped | February | Medium | Sustained
2025-02-18 | 22:05 | 055/25 | Orapa 2 – Serule | Orapa 2 - Serule 220kV Line CB L15 | 220 | Transmission | North | Rain | 23:10 | 1.08 | SCADA / Tsenang | Distance protection: SOTF, Phase A-G, Distance to fault = 48.15 km | February | High | Permanent
2025-02-18 | 22:10 | 056/25 | Rakola – Segoditshane | Rakola - Segs 220kV Line CB L35 | 220 | Transmission | South | Clear | 22:27 | 0.28 | SCADA | 3ph trip + ARC | February | Medium | Sustained
2025-02-18 | 22:50 | 057/25 | Segoditshane – Dwaarsburg | Segs - Dwarsburg 132kV Line CB 905 | 132 | Transmission | South | Rain | 23:02 | 0.2 | SCADA | 3ph trip + L/O | February | Medium | Sustained
2025-02-19 | 17:47 | 063/25 | G-Enclave – Gabsouth | G-Enclave - Gabsouth 132kV Line 1 CB 105 | 132 | Transmission | South | Rain | 20:50 | 3.05 | SCADA / Karabo | CB trip, Inter trip receive | February | High | Permanent
2025-02-21 | 18:06 | 065/25 | Gabsouth – Spitskop | Gabsouth - Spitskop 132kV line CB 505 | 132 | Transmission | South | Rain | 18:24 | 0.3 | SCADA / Kaloso | 3ph trip + L/O | February | Medium | Sustained
2025-02-23 | 20:31 | 066/25 | Phokoje – Serule | Phokoje - Serule 220kV Line CB L35 | 220 | Transmission | North | Rainy | 21:10 | 0.65 | SCADA / Boiditswe | Back up Directional E/F, Zone 3, DTTS; Master trip | February | High | Permanent
2025-02-23 | 20:31 | 066/25 | Orapa 2 – Serule | Orapa 2 - Serule 220kV Line CB L15 | 220 | Transmission | North | Rainy | 21:35 | 1.07 | SCADA / Tsenang | Main 2: Trip, Ph C/Ground, Zone 2, O/C | February | High | Permanent
2025-02-25 | 03:53 | 068/25 | Letlhakane – Morupule B | Letlhakane - Morp B 400kV Line CB 3L5 | 400 | Transmission | Northwest | Rainy | 05:18 | 1.42 | SCADA / Tsenang | Ground Imp trip, Phase A to Ground; Load loss: Motheo (13 MW), KCM (18 MW), Orapa (22 MW) | February | High | Permanent
2025-02-25 | 03:53 | 068/25 | Morupule B – Letlhakane | Morp B - Letlhakane 400kV Line CB 2L5 | 400 | Transmission | Northwest | Rainy | 05:19 | 1.43 | SCADA / Moalosi | General trip, Zm trip, Master trip | February | High | Permanent
2025-02-25 | 04:52 | 069/25 | Orapa 2 | Orapa 2 220/33kV Transformer 1 HV CB H10 | 220 | Transmission | North | Rainy | 06:19 | 1.45 | SCADA / Tsenang | Overvoltage; Gen trip, HV inter trip | February | High | Permanent
2025-02-25 | 04:52 | 069/25 | Legotlhwane – Mawana | Legotlhwane - Mawana 220kV Line CB L15 | 220 | Transmission | Northwest | Rainy | 04:59 | 0.12 | SCADA | 3ph trip + L/O | February | Medium | Sustained
2025-02-25 | 04:52 | 069/25 | Mawana – Legotlhwane | Mawana - Legotlhwane 220kV Line CB L25 | 220 | Transmission | Northwest | Rainy | 05:01 | 0.15 | SCADA / Rasefako | 3ph trip + L/O | February | Medium | Sustained
2025-02-25 | 18:47 | 071/25 | Legotlhwane – Makoba | Legotlhwane - Makoba 132kV line CB 305 | 132 | Transmission | Northwest | Cloudy | 18:48 | 0.02 | SCADA | 3ph T + ARC; Load loss (2.4 MW Makoba, 3 MW Samochima) | February | Low | Transient
2025-02-25 | 18:47 | 071/25 | Makoba – Legotlhwane | Makoba - Legotlhwane 132kV line CB 305 | 132 | Transmission | Northwest | Cloudy | 18:48 | 0.02 | SCADA | 3ph T + ARC | February | Low | Transient
2025-02-28 | 05:04 | 071/A/25 | Phokoje – Matimba | Phokoje - Matimba 400kV line | 400 | Transmission | Central | Clear | 05:45 | 0.68 | SCADA | Blue Phase Impedance E/F; 3 Ph T+L/O | February | High | Permanent
2025-02-28 | 05:04 | 071/A/25 | Phokoje – Insukamini | Phokoje - Insukamini 400kV line | 400 | Transmission | Central | Clear | 06:11 | 1.78 | SCADA | DTTS/R, Master trip; 3 Ph T+L/O | February | High | Permanent
2025-02-28 | 05:32 | 071/A/25 | Gab South – Spitskop | Gab South - Spitskop 132kV line | 132 | Transmission | South | Clear | 06:29 | 0.95 | SCADA | Overload operated; 3 Ph T+L/O | February | High | Permanent
2025-02-28 | 05:32 | 071/A/25 | Gab South – Dwaarsberg | Gab South - Dwaarsberg 132kV line | 132 | Transmission | South | Clear | 06:57 | 1.42 | SCADA | Overload operated; 3 Ph T+L/O | February | High | Permanent
2025-02-28 | 05:32 | 071/A/25 | Segoditshane – Dwaarsberg | Segoditshane - Dwaarsberg 132kV line | 132 | Transmission | South | Clear | 06:34 | 1.03 | SCADA | Overload operated; 3 Ph T+L/O | February | High | Permanent
2025-02-28 | 11:20 | 072/25 | Mogoditshane | Mogoditshane 132/11kV T4 HV CB 510 | 132 | Transmission | South | Clear | 12:30 | 1.17 | SCADA / A. Mangole | No indications; Load loss | February | High | Permanent
2025-03-02 | 4:41 | 074A/25 | Morupule B – Isang 400kV line | Morupule B - Isang 400kV Line CB 1L5 | 400 | Transmission | Central/South | Rainy | 06:22 | 1.68 | SCADA | Trip, General trip, Zm trip | March | High | Permanent
2025-03-02 | 4:41 | 074A/25 | Isang – Morupule B 400kV line | Isang - Morupule B 400kV Line CB 4L5 | 400 | Transmission | Central/South | Rainy | 06:23 | 1.7 | SCADA / Kaloso | Carrier Aided trip, Permissive trip S/R | March | High | Permanent
2025-03-03 | 18:23 | 074C/25 | Gabsouth – Spitskop 132kV line | Gabsouth - Spitskop 132kV Line CB 505 | 132 | Transmission | South | Clear | 19:33 | 1.17 | SCADA | 3Ph T + L/O | March | High | Permanent
2025-03-03 | 18:23 | 074C/25 | Spitskop – Gabsouth 132kV line | Spitskop - Gabsouth 132kV Line CB (unspecified) | 132 | Transmission | South | Clear | 19:23 | 1 | SCADA / Galetshetse | 3Ph T + L/O | March | High | Permanent
2025-03-03 | 22:27 | 076/25 | Morupule B – Isang 400kV line | Morupule B - Isang 400kV Line CB 1L5 | 400 | Transmission | Central/South | Cloudy | 0:29 | 0.08 | SCADA | 3Ph T + L/O | March | Low | Transient
2025-03-03 | 0:24 | 076/25 | Isang – Morupule B 400kV line | Isang - Morupule B 400kV Line CB 4L5 | 400 | Transmission | Central/South | Cloudy | 0:29 | 0.08 | SCADA / Galetshetse | Main 1: 3ph trip, Carrier Aided trip, fault loop L3-N, distance to fault 34.3 km | March | Low | Transient
2025-03-07 | 13:15 | 078/25 | Tsabong – Heuningflei 132kV line | Tsabong - Heuningflei 132kV Line CB 105 | 132 | Transmission | South | Raining | 19:05 | 5.83 | Mosarwe | Trip, Zone 1, Ground | March | High | Permanent
2025-03-09 | 18:30 | 077/25 | Gabsouth – Ramotswa 132kV line | Gabsouth - Ramotswa 132kV Line CB 205 | 132 | Transmission | South | Clear | 21:11 | 2.68 | SCADA / K. Gaboitsiwe | backup protection – E/F trip, master trip | March | High | Permanent
2025-03-09 | 18:30 | 077/25 | Ramotswa – Gabsouth 132kV line | Ramotswa - Gabsouth 132kV Line CB 205 | 132 | Transmission | South | Clear | 21:11 | 2.68 | SCADA / K. Kaloso | 3Ph trip + L/O | March | High | Permanent
2025-03-09 | 18:30 | 077/25 | Ramotswa, 132kV Bus section | Ramotswa 132kV Bus Section CB 120 | 132 | Transmission | South | Clear | 1:31 | 7.02 | SCADA / K. Kaloso | master trip, TCS 1 and 2, start, trip | March | High | Permanent
2025-03-09 | 18:30 | 077/25 | Tlokweng – Gabsouth 132kV line | Tlokweng - Gabsouth 132kV Line CB 105 | 132 | Transmission | South | Clear | 20:58 | 2.47 | SCADA / R. Galetshetse | diff trip, instant E/F trip, O/C start, E/F start, DTTR, phase L1, L2 | March | High | Permanent
2025-03-09 | 18:30 | 077/25 | Tlokweng, 132kV Bus Section | Tlokweng 132kV Bus Section CB 120 | 132 | Transmission | South | Clear | 2:26 | 7.93 | SCADA / R. Galetshetse | Tripped | March | High | Permanent
2025-03-09 | 18:30 | 077/25 | Gabsouth – Kgale View 132kV line | Gabsouth - Kgale View 132kV Line CB 605 | 132 | Transmission | South | Clear | 20:27 | 1.95 | SCADA | Backup and O/C relay: E/F trip; Fault mag: IA=134A, IB=139A, IC=1810A, IN=1560A | March | High | Permanent
2025-03-09 | 18:30 | 077/25 | Government Enclave, 132/11kV T1 | Government Enclave 132/11kV T1 HV CB 180 | 132 | Transmission | South | Clear | 19:55 | 1.42 | SCADA | 132 kV multiplication and E/F relay: E/F trip | March | High | Permanent
2025-03-10 | 3:12 | 079/25 | Morupule B – Isang 400kV line | Morupule B - Isang 400kV Line CB 1L5 | 400 | Transmission | Central/South | Clear | 5:56 | 2.73 | SCADA / Moalosi | Blue phase Impedance trip | March | High | Permanent
2025-03-10 | 3:12 | 079/25 | Isang – Morupule B 400kV line | Isang - Morupule B 400kV Line CB 4L5 | 400 | Transmission | Central/South | Clear | 5:55 | 2.72 | SCADA / Kaloso | Blue phase Impedance trip, Carrier Aided trip, Permissive trip S/R | March | High | Permanent
2025-03-13 | 13:01 | 078/25 | Francistown | Francistown 220/11kV TX 1B HV CB H20 | 220 | Transmission | North | Cloudy | 14:12 | 1.18 | SCADA / Chaiwilani | F/town, 220/11kV TX 1B HV side | March | High | Permanent
2025-03-13 | 13:01 | 078/25 | Hydromet – Francistown 220kV line | Hydromet - Francistown 220kV Line CB L25 | 220 | Transmission | North | Cloudy | 14:47 | 1.77 | SCADA / Moreetsi | Backup trip, O/C to ground | March | High | Permanent
2025-03-13 | 13:01 | 078/25 | Morupule A – Serule 220kV line | Morupule A - Serule 220kV Line CB (unspecified) | 220 | Transmission | North | Cloudy | 14:25 | 1.4 | SCADA / Moalosi | Main 1 trip, 21L trip, DTT, Zone 1 trip; Distance to fault: 79.56 km | March | High | Permanent
2025-03-13 | 13:01 | 078/25 | Serule – Morupule 220kV line | Serule - Morupule 220kV Line CB (unspecified) | 220 | Transmission | North | Cloudy | 14:25 | 1.4 | SCADA / Sekgatlhola | 3-phase trip + Lockout | March | High | Permanent
2025-03-13 | 14:35 | 078/25 | Lobatse – Mmakgodumo 132kV line | Lobatse - Mmakgodumo 132kV Line CB 205 | 132 | Transmission | South | Rainy | 14:36 | 0.02 | SCADA | Current Diff, White phase Impedance E/F; 3Ph trip + L/O | March | Low | Transient
2025-03-13 | 14:35 | 078/25 | Mmakgodumo – Lobatse 132kV line | Mmakgodumo - Lobatse 132kV Line CB 205 | 132 | Transmission | South | Rainy | 14:36 | 0.02 | SCADA | 3Ph trip + L/O | March | Low | Transient
2025-03-13 | 21:33 | 079/25 | Motheo – Motheo Mine 132kV line | Motheo - Motheo Mine 132kV Line CB 305 | 132 | Transmission | North West | Clear | 21:41 | 0.13 | SCADA / Kahona | Red, White and Blue TCS operated | March | Medium | Sustained
2025-03-13 | 21:33 | 079/25 | Ghanzi – Motheo 132kV line | Ghanzi - Motheo 132kV Line CB 205 | 132 | Transmission | North West | Clear | 21:44 | 0.18 | SCADA | Main 1 protection trip L1, L2, L3. General trip | March | Medium | Sustained
2025-03-13 | 21:40 | 080/25 | Morupule B – Isang 400kV line | Morupule B - Isang 400kV Line CB 1L5 | 400 | Transmission | Central/South | Clear | 23:42 | 2.03 | SCADA / Moalosi | Main A & B: trip, general trip, Z-trip; Fault loop L3-N; Distance to fault 126.71 km | March | High | Permanent
2025-03-13 | 21:40 | 080/25 | Isang – Morupule B 400kV line | Isang - Morupule B 400kV Line CB 4L5 | 400 | Transmission | Central/South | Clear | 23:43 | 2.05 | SCADA / Galetshetse | Main 1: 3ph trip, Carrier Aided trip, fault loop L3-N, distance to fault 58.81 km | March | High | Permanent
2025-03-13 | 23:03 | 081/25 | Motheo – Motheo Mine 132kV line | Motheo - Motheo Mine 132kV Line CB 305 | 132 | Transmission | North West | Clear | 23:07 | 0.07 | SCADA / Kahona | Red, White and Blue TCS operated | March | Low | Transient
2025-03-13 | 23:03 | 081/25 | Ghanzi – Motheo 132kV line | Ghanzi - Motheo 132kV Line CB 205 | 132 | Transmission | North West | Clear | 23:07 | 0.07 | SCADA | Main 1 protection trip L1, L2, L3. General trip | March | Low | Transient
2025-03-16 | 13:54 | 85/25 | Gabsouth | Gabsouth 132/11kV Tx 2 HV CB 310 | 132 | Transmission | South | Clear | 16:06 | 2.2 | SCADA / K. Kaloso | Main 1 and 2 DIFF trip operated, REF operated | March | High | Permanent
2025-03-16 | 13:54 | 85/25 | Gabsouth | Gabsouth 132/11kV Tx 2 LV CB 2HO | 132 | Transmission | South | Clear | 16:06 | 2.2 | SCADA / K. Kaloso | External B/UP trip operated, aster trip operated | March | High | Permanent
2025-03-18 | 3:49 | 87/25 | Morupule B – Isang 400kV line | Morupule B - Isang 400kV Line CB 1L5 | 400 | Transmission | Central/South | Clear | 4:47 | 0.97 | SCADA / Moalosi | Main A and B: Trip, General trip, ZM trip, Fault loop L1-N; Distance to fault 154.26 km | March | High | Permanent
2025-03-18 | 3:49 | 87/25 | Isang – Morupule B 400kV line | Isang - Morupule B 400kV Line CB 4L5 | 400 | Transmission | Central/South | Clear | 4:47 | 0.97 | SCADA / Galetshetse | Main 1: 3ph trip, Carrier aided trip, Fault loop L1-N, Distance to fault 42.77 km | March | High | Permanent
2025-03-23 | 19:55 | 88/25 | Phokoje – Mmadinare 220kV line | Phokoje - Mmadinare 220kV Line CB L25 | 220 | Transmission | North | Rainy | 19:59 | 0.07 | SCADA | 3ph trip + L/O | March | 0.02 | FALSE
2025-03-23 | 19:55 | 88/25 | Serule – Phokoje 220kV line | Serule - Phokoje 220kV Line CB L35 | 220 | Transmission | North | Rainy | 19:59 | 0.07 | SCADA | — | March | Low | Transient
2025-03-31 | 22:57 | 092/25 | Mawana – Letlhakane 400kV line | Mawana - Letlhakane 400kV Line CB 2L5 | 400 | Transmission | North West | Normal | 23:06 | 0.15 | SCADA / Rasefako | Main 1: Phase A to Ground, Ground Impedance trip; 3ph trip + L/O | March | Medium | Sustained
2025-03-31 | 22:57 | 092/25 | Letlhakane – Mawana 400kV line | Letlhakane - Mawana 400kV Line CB 1L5 | 400 | Transmission | North West | Normal | 23:07 | 0.17 | SCADA / Tsenang | Main 1 & 2: 3ph trip, Zone 1, SOTF, Carrier aided trip, AR Successful | March | Medium | Sustained
2025-04-08 | 14:11 | 095/25 | Woodhall – Lobatse 132kV line | Woodhall - Lobatse 132kV Line CB 105 | 132 | Transmission | South | Rainy | 16:12 | 2.02 | Ntoko | B/U Protection Relay; Blue phase Impedance E/F; 3 ph T + L/O | April | High | Permanent
2025-04-09 | 9:03 | 096/25 | F/town – Dukwe 132kV line | F/town - Dukwe 132kV Line CB 205 | 132 | Transmission | South | Rainy | 10:06 | 1.05 | SCADA / Magola | Distance to fault 75.9km, Zone 1 trip, TRC, Zm1/2/3; Fault loop R-N; CRZ, CFZ | April | High | Permanent
2025-04-11 | 9:19 | 96/25 | Morupule B – Isang 400kV line | Morupule B - Isang 400kV Line CB 1L5 | 400 | Transmission | Central/South | Clear | 10:09 | 0.83 | SCADA / Moalosi | Main A & B: Trip, General trip, ZM trip, Fault loop L1-N; Distance to fault 9.31 km | April | High | Permanent
2025-04-11 | 9:19 | 96/25 | Isang – Morupule B 400kV line | Isang - Morupule B 400kV Line CB 4L5 | 4000 | Transmission | Central/South | Clear | 10:07 | 0.8 | SCADA / Galetshetse | Main 1: 3ph trip, Carrier aided trip, Fault loop L1-N, Distance to fault 134.35 km | April | High | Permanent
2025-04-19 | 7:12 | 102/25 | Orapa – Orapa 2 220kV line | Orapa - Orapa 2 220kV Line CB L15 | 220 | Transmission | North | Cloudy | 8:10 | 0.97 | SCADA / Tsenang | Trip, Zone 1, 50/51 (ph diff O/C); Pole discrepancy | April | High | Permanent
2025-04-19 | 21:35 | 100/25 | Phokoje – Matimba 400kV line | Phokoje - Matimba 400kV Line CB 3L5 | 400 | Transmission | Central | Clear | 21:59 | 0.4 | SCADA / Sekgatlhola | Blue phase Impedance E/F, Zone 1 Ext; Distance to fault 210 km | April | Medium | Sustained
2025-04-19 | 21:35 | 100/25 | Phokoje – Insukamini 400kV line | Phokoje - Insukamini 400kV Line CB 2L5 | 400 | Transmission | Central | Clear | 22:10 | 0.58 | SCADA / Sekgatlhola | DTTR/S, master trip | April | High | Permanent
2025-04-19 | 21:35 | 100/25 | Insukamini – Phokoje 400kV line | Insukamini - Phokoje 400kV Line CB (unspecified) | 400 | Transmission | Central | Clear | 22:10 | 0.58 | SCADA / ZESA | 3ph T + L/O | April | High | Permanent
2025-05-04 | 5:11 | 107/25 | Morupule B – Isang 400kV line | Morupule B - Isang 400kV Line CB 1L5 | 400 | Transmission | Central/South | Cloudy | 5:17 | 0.1 | SCADA / Moalosi | Main A & B: Trip, General trip, ZM trip; Fault loop L2-N; Distance to fault 78.59 km | May | Medium | Sustained
2025-05-04 | 5:11 | 107/25 | Isang – Morupule B 400kV line | Isang - Morupule B 400kV Line CB 4L5 | 400 | Transmission | Central/South | Cloudy | 5:17 | 0.1 | SCADA / Galetshetse | Z1 Impedance Trip, Permissive Trip receive | May | Medium | Sustained
2025-05-07 | 13:57 | 009/25 | Legotlhwane – Makoba 132kV line | Legotlhwane - Makoba 132kV Line CB 305 | 132 | Transmission | North West | Cloudy | 19:27 | 5.5 | SCADA / K. Mosala | 3 ph Trip + L/O | May | High | Permanent
2025-05-07 | 15:53 | 110/25 | Morupule A – Isang 220kV line | Morupule A - Isang 220kV Line 2 CB L25 | 220 | Transmission | North | Clear | 17:27 | 1.57 | SCADA / Moalosi | Main 1: C/B fail, A-G trip, distance to fault 6.02 km; Main B: Z1 trip | May | High | Permanent
2025-05-13 | 6:07 | 113/25 | Dukwe – Sua Pan 132kV line | Dukwe - Sua Pan 132kV Line CB 305 | 132 | Transmission | South | Clear | 6:43 | 0.6 | SCADA / Chabalala | Tripped | May | High | Permanent
2025-05-22 | 19:38 | 115/25 | Thamaga – Rakola 220kV line | Thamaga - Rakola 220kV Line CB L45 | 220 | Transmission | South | Clear | 19:45 | 0.12 | SCADA | IMP PROTECTION START ZONE 1, LINE DIFF PROTECTION TRIP; 3ph trip + L/O | May | Medium | Sustained
2025-05-23 | 1:32 | 116/25 | Thamaga – Rakola 220kV line | Thamaga - Rakola 220kV Line CB L45 | 220 | Transmission | South | Clear | 1:33 | 0.02 | SCADA | 3ph trip + L/O | May | Low | Transient
2025-05-31 | 23:35 | 117/25 | Morupule A – Serule 220kV line | Morupule A - Serule 220kV Line CB L55 | 220 | Transmission | North | Clear | 1:15 | 1.67 | SCADA / Moalosi | Main A: ABC trip, 21L, DTT, Zone 1; Main B: DTT, SOTF; Fault location 17.33 km | May | High | Permanent
2025-05-31 | 23:35 | 117/25 | Serule – Morupule A 220kV line | Serule - Morupule A 220kV Line CB L65 | 220 | Transmission | North | Clear | 1:21 | 1.77 | SCADA / Likokotlo | Main A: 3ph trip, Lockout relay 1 & 2, DTT; Main B: 3ph trip, DTT, SOTF | May | High | Permanent
2025-05-31 | 23:35 | 117/25 | Serule – Phokoje 220kV line | Serule - Phokoje 220kV Line CB L95 | 220 | Transmission | North | Clear | 23:39 | 0.07 | SCADA / Likokotlo | Main A: 3ph trip, Lockout relay 1 & 2, DTT; Main B: 3ph trip, DTT, SOTF | May | Low | Transient
2025-05-31 | 23:35 | 117/25 | Phokoje – Serule 220kV line | Phokoje - Serule 220kV Line CB L35 | 220 | Transmission | North | Clear | 5:22 | 5.78 | SCADA / Likokotlo | No indications; 3ph trip + L/O | May | High | Permanent
2025-06-02 | 3:03 | 118/25 | Morupule B – Isang 400kV line | Morupule B - Isang 400kV Line CB 1L5 | 400 | Transmission | Central/South | Clear | 3:05 | 0.03 | SCADA | 3ph trip + L/O | June | Low | Transient
2025-06-02 | 3:03 | 118/25 | Isang – Morupule B 400kV line | Isang - Morupule B 400kV Line CB 4L5 | 400 | Transmission | Central/South | Clear | 3:08 | 0.08 | SCADA | VT Fuse fail, 3ph trip, Carrier aided trip; Distance to fault 50.1 km | June | Low | Transient
2025-06-02 | 19:38 | 119/25 | Thamaga – Rakola 220kV line | Thamaga - Rakola 220kV Line CB L45 | 220 | Transmission | South | Clear | 19:45 | 0.12 | SCADA | IMP PROTECTION START ZONE 1, LINE DIFF PROTECTION TRIP; 3ph trip + L/O | June | Medium | Sustained
2025-06-13 | 22:02 | 124/25 | Morupule B – Isang 400kV line | Morupule B - Isang 400kV Line CB 1L5 | 400 | Transmission | Central/South | Clear | 22:19 | 0.28 | SCADA | A& B Trip, General trip, ZM trip; Distance to fault 81.15km, fault loop L2-N | June | Medium | Sustained
2025-06-13 | 22:02 | 124/25 | Isang – Morupule B 400kV line | Isang - Morupule B 400kV Line CB 4L5 | 400 | Transmission | Central/South | Clear | 22:19 | 0.28 | SCADA | 3ph trip + L/O | June | Medium | Sustained
2025-06-23 | 9:48 | 125/25 | Morupule B – Isang 400kV line | Morupule B - Isang 400kV Line CB 1L5 | 400 | Transmission | Central/South | Clear | 9:54 | 0.1 | SCADA | Main A & B: Trip, General trip, ZM trip; Distance to fault 148.63km, fault loop L2-N | June | Medium | Sustained
2025-06-23 | 9:48 | 125/25 | Isang – Morupule B 400kV line | Isang - Morupule B 400kV Line CB 4L5 | 400 | Transmission | Central/South | Clear | 9:54 | 0.1 | SCADA | Main 1 & 2: 3ph trip, Carrier aided trip; Fault loop L2-N | June | Medium | Sustained
2025-06-24 | 23:14 | 126/25 | Morupule B – Isang 400kV line | Morupule B - Isang 400kV Line CB 1L5 | 400 | Transmission | Central/South | Clear | 23:18 | 0.07 | SCADA | Main A & B: Trip, General trip, ZM trip; Distance to fault 86.0km, fault loop L3-N | June | Low | Transient
2025-06-24 | 23:14 | 126/25 | Isang – Morupule B 400kV line | Isang - Morupule B 400kV Line CB 4L5 | 400 | Transmission | Central/South | Clear | 23:18 | 0.07 | SCADA | Main 1 & 2: 3ph trip, Carrier aided trip; Fault loop L3-N | June | Low | Transient
2025-06-25 | 6:24 | 127/25 | Morupule B – Isang 400kV line | Morupule B - Isang 400kV Line CB 1L5 | 400 | Transmission | Central/South | Clear | 6:31 | 0.12 | SCADA | Main A & B: Trip, General trip, ZM trip; Distance to fault 148.63km, fault loop L3-N | June | Medium | Sustained
2025-06-25 | 6:24 | 127/25 | Isang – Morupule B 400kV line | Isang - Morupule B 400kV Line CB 4L5 | 400 | Transmission | Central/South | Clear | 6:31 | 0.12 | SCADA | Main 1 & 2: 3ph trip, Carrier aided trip; Fault loop L3-N | June | Medium | Sustained
2025-06-25 | 17:31 | 128/25 | Molepolole | Molepolole 132/33kV T1 HV CB 110 | 132 | Transmission | South | Clear | 20:48 | 3.28 | Kgame/Galetshetse | Phases B & C to ground | June | High | Permanent